## Weekly Data
2001 - BUFFALO POUND WATER QUALITY DATA
RAW LAKE WATER
Parameters | Units | time axis 2001-01-01 to 2001-12-24
|  |  |  | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to
 | time axis 2001-01-05 to 2001-12-28
|  | current year chart | [53 empty] | Weekly Routine Tests Done - not including bacteria, algae, chemical doses or chlorine residuals (done daily and are determined seperately) | time axis 2001-01-05 to 2001-12-28
PHYSICAL
Colour (Apparent) | Pt/Co |  |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 20 | 40 | 30 |  | 35 | 25 | 50 | 30 | 40 | 40 | 30 | 30 | 50 | 30 | 50 | 50 | 50 | 60 | 30 | 70 | 50 | 20 | 60 | 60 | 50 | 50 | 60 | 50 | 60 | 80 | 35 | 30 | 80 | 30 | 25 | 20 | 15 | 10 | 20 |  | 49
Conductivity | µS/cm |  |  | 702 | 710 | 707 | 713 | 718 | 719 | 726 | 739 |  | 745 | 749 | 741 | 728 | 720 | 707 |  | 739 | 563 | 574 | 587 | 584 | 590 | 599 | 605 | 586 | 576 | 575 | 582 | 564 | 543 | 543 | 529 | 509 | 523 | 524 | 524 | 530 | 522 | 519 | 525 | 532 | 539 | 542 | 548 | 547 | 547 | 550 | 557 | 577 | 598 | 610 |  | 49
Bench Diss. Oxygen | mg/L |  |  | 9.8 | 8.8 | 8.1 | 7.4 | 7.7 | 6.7 | 6.3 | 6.3 |  | 5.9 | 3.7 | 4.2 | 5.8 | 7 | 7 | 11.2 | 8.3 | 10.3 | 9.8 | 9.1 | 9.3 | 8.7 | 8.7 | 8.9 | 9.2 | 9.1 | 8 | 6.5 | 7.8 | 7 | 6.7 | 7.1 | 6.4 | 7.1 | 8 | 8.6 | 7.9 | 8.9 | 9.3 | 10.2 | 10.2 | 10.4 | 11.2 | 11.7 | 11.7 | 11.7 | 12.4 | 12.4 | 10.4 | 11.4 | 10.5 | 11.3 | 51
Bench Diss. Oxygen | % | CY Chart |  | 72.6464 | 65.0888 | 60.5381 | 55.6391 | 57.4198 | 50.2249 | 47.619 | 47.2264 | uncalcuable | 44.4612 | 28.2012 | 31.5789 | 44.8916 | 54.7731 | 55.6439 | 90.9091 | 68.7086 | 87.2142 | 88.9292 | 88.9541 | 87.1603 | 87.9676 | 87.0871 | 92.5156 | 96.0334 | 100.8869 | 86.7679 | 72.87 | 88.1356 | 80.9249 | 76.1364 | 83.5294 | 71.9101 | 79.7753 | 88.3002 | 91.1983 | 80.203 | 88.6454 | 89.5091 | 100.7905 | 90.4255 | 84.4156 | 89.7436 | 88.6364 | 89.3812 | 87.2483 | 91.1765 | 85.9321 | 73.7589 | 81.7204 | 76.5864 | 83.0882 | 51
ON-LINE Diss. Oxygen | % | CY Chart |  | 99 | 89 |  | 61 | 57 | 53 | 49 | 45 |  | 35 | 27 | 39 | 66 | 54 | 61 | 102 | 91 | 93.5 | 88.1 | 88.6 | 88 | 87.3 | 88.7 | 84.4 | 94.6 | 102 | 100.5 | 99 | 89.2 | 80.6 | 69.1 | 84.7 | 65 | 77 | 86.1 | 87.8 | 73.8 | 98 | 97.1 | 111.4 | 97.8 | 97.8 | 94.5 | 88.6 | 80.4 | 97.4 | 95 | 98 |  | 92 | 81.4 | 89.8 | 49
Odour | T.O.N. | CY Chart |  | 12 | 16 | 12 | 14 |  | 10 |  | 18 |  | 10 |  | 14 | 35 | 55 | 190 | 100 | 200 | 130 | 85 | 90 | 80 | 100 | 85 | 150 | 200 | 325 | 166 | 200 | 87 | 93 | 125 | 95 | 112 | 95 | 150 | 144 | 122 | 80 | 60 | 80 | 43 | 50 | 30 | 16 | 19 | 22 | 17 | 27 | 16 | 27 | 30 |  | 47
Particles | per ml |  |  | 10932 | 11262 | 8839 | 9703 | 10059 |  |  | 13878 |  | 13723.6 | 17958 |  | 48513 |  | 57509 |  | 44213 | 41369 | 58066 | 55021 | 55514 | 58341.66 | 41881.64 | 52029 | 50880 | 55272.06 | 63356 | 34418 | 48895 | 58388 | 68738 | 54115 | 42652 | 40529 | 33701 | 37629 | 30012 | 50392 | 39781 | 45469 | 75906 |  | 29166 | 40910 | 53712 | 37036 | 29650 |  | 13489 | 14572 | 16550 |  | 43
pH | pH units |  |  | 7.99 | 7.81 | 7.73 | 7.85 | 7.7 | 7.62 | 7.71 | 7.74 |  | 7.54 | 7.49 | 7.63 | 7.59 | 7.59 | 7.56 | 7.84 | 7.7 | 8.08 | 8.21 | 8.24 | 8.29 | 8.27 | 8.29 | 8.31 | 8.42 | 8.46 | 8.43 | 8.11 | 8.41 | 8.23 | 8.38 | 8.5 | 8.58 | 8.42 | 8.55 | 8.44 | 8.35 | 8.36 | 8.4 | 8.61 | 8.55 | 8.45 | 8.34 | 8.22 | 8.12 | 8.08 | 8.27 | 8.22 | 7.92 | 8.11 | 8.03 | 7.93 | 51
SST | mg/L |  |  |  | 2.4 | 2.5 | 2.1 |  | 2.5 |  | 2.2 |  | 1.9 |  | 2.1 | 4 |  | 9 |  | 8.8 | 6.2 | 19.8 | 7.2 | 6 | 9 | 16 | 15.4 | 16.6 | 10 | 16 | 10.6 | 12.2 | 15.8 | 18.2 | 14.8 | 11 | 13 | 13.4 | 16.4 | 12.8 | 12.6 | 16.8 | 19.4 | 19.2 | 45.6 | 12.2 | 14.2 | 16.6 | 11.6 | 10.2 | 5.2 | 4.8 | 2.8 | 4.6 |  | 44
SSV | mg/L |  |  |  | 1.2 | 1.2 | 0.8 |  | 0.9 |  | 0.9 |  | 0.7 |  | 1.3 | 2.4 |  | 4.8 |  | 5.4 | 3.2 | 5.3 | 3.3 | 2 | 3 | 4.6 | 5.4 | 7.2 | 6.6 | 3.6 | 5 | 5.6 | 6.5 | 8.2 | 8.2 | 6.8 | 8.6 | 9.8 | 12.4 | 9.4 | 9.4 | 11.4 | 15.2 | 13.4 | 20.8 | 6.8 | 2.4 | 3 | 2.8 | 2.4 | 1.6 | 2.3 | 1.6 | 2.3 |  | 44
SSF | mg/L |  |  |  | 1.2 | 1.3 | 1.3 |  | 1.6 |  | 1.3 |  | 1.2 |  | 0.8 | 1.6 |  | 4.2 |  | 3.4 | 3 | 14.5 | 3.9 | 4 | 6 | 11.4 | 10 | 9.4 | 3.4 | 8.8 | 5.6 | 6.6 | 9.3 | 10 | 6.6 | 4.2 | 4.4 | 3.6 | 4 | 3.4 | 3.2 | 5.4 | 4.2 | 5.8 | 24.8 | 5.4 | 11.8 | 13.6 | 8.8 | 7.8 | 3.6 | 2.5 | 1.2 | 2.3 |  | 44
Temperature | ° C |  |  | 2.9 | 2.8 | 3.2 | 3.4 | 3.1 | 3.3 | 3.6 | 3.3 |  | 3.5 | 3.9 | 3.4 | 4.5 | 4.9 | 5.5 | 6.3 | 7.1 | 8 | 10.9 | 14.2 | 12.3 | 15.8 | 15.3 | 17.1 | 17.3 | 20.3 | 19.2 | 20.9 | 21.3 | 22.5 | 21.6 | 23.4 | 21 | 21 | 20.1 | 18.1 | 16 | 15.1 | 13.5 | 14.7 | 9.9 | 6.3 | 5.8 | 3.7 | 4 | 3.1 | 2.6 | 0.5 | 1.3 | 1.7 | 2.3 | 2.6 | 51
Turbidity | NTU |  |  | 2.37 | 2.36 | 2.04 | 1.88 | 2.01 | 2.27 | 1.97 | 2.21 |  | 2 | 2.07 | 1.69 | 2.37 | 4.1 | 3.9 | 4.72 | 5.59 | 5.5 | 13.4 | 4.7 | 9.75 | 5.54 | 10.1 | 10.9 | 15.7 | 13.3 | 9.28 | 8.85 | 8.31 | 13.3 | 14.3 | 12.3 | 10.3 | 7.07 | 15.4 | 16 | 6.2 | 5.25 | 7.9 | 8.21 | 9.58 | 19.1 | 5.95 | 6.04 | 19.2 | 8.2 | 6.1 | 3.19 | 3.23 | 1.84 | 2.87 | 5.16 | 51
TDS | mg/L(calc) |  |  | uncalcuable | 566.2 | 567.6 | 568.13 | 577.14 | 577.04 | uncalcuable | 584.99 | uncalcuable | 597.8 | 601.25 | 594.09 | 590.57 | 576.36 | 570.98 | 568.4 | 597.36 | 446.28 | 449.7 | 463.84 | 467.86 | 476.64 | 480.9 | 483.32 | 467.84 | 455.44 | uncalcuable | 454.59 | 451.9 | 408.69 | 423.56 | 407.2 | 405.95 | 411.1 | 411.46 | 412.04 | 417.52 | 409.49 | 411.42 | 413 | 412.09 | 427.2 | 428.73 | 426.72 | 433.91 | 431 | 438 | 437.65 | 459.14 | 472.02 | 482.32 | uncalcuable | 47
Langelier Index (RTW) | pH units (calc) | CY Chart |  |  | 0.15842 | 0.084963 | 0.21253 | 0.074195 | -0.013592 |  | 0.12939 |  | -0.04368 | -0.0855 | 0.043215 | 0.024264 | 0.012275 | -0.018374 | 0.25987 | 0.18194 | 0.36575 | 0.53314 | 0.64092 | 0.67436 | 0.71858 | 0.74878 | 0.78727 | 0.85826 | 0.89719 |  | 0.55057 | 0.88278 | 0.60672 | 0.76884 | 0.88611 | 0.97961 | 0.78319 | 0.89586 | 0.7607 | 0.64127 | 0.63945 | 0.67936 | 0.91022 | 0.80381 | 0.6509 | 0.55083 | 0.38707 | 0.308 | 0.26235 | 0.44152 | 0.37573 | 0.1121 | 0.34383 | 0.28192 |  | 47
MAJOR CONSTITUENTS
Alkalinity(p) | mg/L CaCO3 | CY Chart |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 4 | 2 | 3 | 0 | 1 | 5 | 2 | 3 | 5 | 2 | 5 | 5 | 0 | 2 | 4 | 7 | 5 | 4 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 50
Alkalinity(total) | mg/L CaCO3 | CY Chart |  | 204 | 202 | 202 | 204 | 206 | 204 | 206 | 209 |  | 215 | 216 | 214 | 215 | 208 | 209 | 205 | 218 | 163 | 170 | 168 | 170 | 175 | 176 | 176 | 168 | 160 | 155 | 158 | 161 | 138 | 144 | 140 | 146 | 144 | 146 | 144 | 145 | 145 | 150 | 151 | 154 | 157 | 157 | 157 | 160 | 160 | 163 | 164 | 171 | 176 | 180 |  | 50
Bicarbonate | mg/L | CY Chart |  | 249 | 246 | 246 | 249 | 251 | 249 | 251 | 255 |  | 262 | 263 | 261 | 262 | 254 | 255 | 250 | 266 | 199 | 207 | 205 | 207 | 213 | 214 | 210 | 195 | 190 | 181 | 193 | 194 | 156 | 170 | 163 | 166 | 170 | 166 | 163 | 177 | 172 | 173 | 167 | 171 | 182 | 184 | 189 | 195 | 195 | 199 | 200 | 208 | 214 | 219 |  | 50
Carbonate | mg/L | CY Chart |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5 | 2 | 4 | 0 | 1 | 6 | 2 | 4 | 6 | 2 | 6 | 6 | 0 | 2 | 5 | 8 | 6 | 5 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 50
Calcium | mg/L | CY Chart |  |  | 61 | 61 | 61 | 63 | 62 |  | 64 |  | 66 | 66 | 66 | 66 | 65 | 63 | 62 | 66 | 51 | 48 | 52 | 53 | 53 | 55 | 54 | 51 | 48 | 52 | 48 | 50 | 44 | 45 | 43 | 46 | 43 | 42 | 43 | 43 | 43 | 44 | 44 | 46 | 46 | 48 | 47 | 48 | 49 | 48 | 50 | 51 | 54 | 54 |  | 48
Magnesium | mg/L | CY Chart |  |  | 27 | 27 | 26 | 26 | 27 |  | 27 |  | 27 | 28 | 27 | 26 | 26 | 26 | 28 | 28 | 20 | 19 | 22 | 20 | 21 | 20 | 21 | 21 | 20 | 18 | 20 | 17 | 18 | 21 | 19 | 17 | 19 | 20 | 19 | 19 | 19 | 20 | 20 | 19 | 20 | 19 | 20 | 20 | 19 | 20 | 19 | 22 | 21 | 23 |  | 48
Hardness (total) | mg/L CaCO3 | CY Chart |  |  | 265 | 262 | 261 | 266 | 266 |  | 272 |  | 276 | 280 | 276 | 273 | 270 | 265 | 270 | 279 | 209 | 200 | 222 | 216 | 220 | 221 | 222 | 212 | 202 | 204 | 205 | 199 | 185 | 199 | 185 | 185 | 186 | 186 | 186 | 187 | 188 | 190 | 192 | 194 | 197 | 198 | 200 | 201 | 202 | 204 | 204 | 217 | 223 | 229 |  | 48
Sodium | mg/L | CY Chart |  |  | 53 | 54 | 54 | 54 | 54 |  | 54 |  | 55 | 56 | 54 | 53 | 54 | 53 | 52 | 56 | 41 | 42 | 44 | 44 | 44 | 45 | 46 | 46 | 46 |  | 45 | 45 | 43 | 42 | 41 | 40 | 41 | 40 | 42 | 40 | 39 | 37 | 39 | 38 | 39 | 39 | 38 | 39 | 38 | 38 | 38 | 40 | 41 | 42 |  | 47
Potassium | mg/L | CY Chart |  |  | 6.4 | 6 | 6.1 | 7.2 | 7.8 |  | 6.4 |  | 5.5 | 5.5 | 5.7 | 5.5 | 5.7 | 5.3 | 5.3 | 5.7 | 4.3 | 4.4 | 4.6 | 5 | 4.8 | 4.8 | 5 | 5.1 | 5.1 |  | 5 | 4.9 | 4.8 | 4.9 | 4.6 | 4.5 | 4.5 | 4.6 | 4.4 | 4.4 | 4.3 | 4.2 | 4.3 | 4.2 | 4.2 | 4.2 | 4 | 4 | 4 | 4 | 4 | 4.2 | 4.2 | 4.2 |  | 47
Sulphate | mg/L | CY Chart |  |  | 151 | 151 | 150 | 153 | 154 |  | 155 |  | 158 | 158 | 156 | 154 | 149 | 146 | 148 | 152 | 114 | 112 | 118 | 121 | 122 | 123 | 126 | 125 | 124 |  | 122 | 119 | 116 | 117 | 111 | 105 | 109 | 110 | 111 | 111 | 108 | 106 | 108 | 105 | 108 | 108 | 106 | 107 | 105 | 107 | 106 | 112 | 115 | 117 |  | 47
Chloride | mg/L | CY Chart |  |  | 14.4 | 14.3 | 14.3 | 14.6 | 14.7 |  | 14.8 |  | 15.1 | 15.2 | 15 | 14.9 | 14.3 | 14.2 | 14.6 | 14.9 | 11.2 | 11.1 | 11.7 | 12 | 12.2 | 12.5 | 12.6 | 12.6 | 12.3 |  | 12.4 | 12 | 11.7 | 12 | 11.2 | 10.8 | 11.1 | 11.2 | 11.3 | 11.5 | 11.1 | 10.8 | 11.1 | 10.8 | 11.5 | 11.1 | 10.9 | 11 | 10.8 | 11.1 | 11 | 11.5 | 11.8 | 12 |  | 47
TRACE CONSTITUENTS
Aluminum (dissolved 0.45µ) | ugL | CY Chart |  | 13 | 59 | 36 | 12 | 8 | 17 |  | 7 |  | 0 | 6 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 11 | 16 | 8 | 0 | 28 | 30 | 29 |  | 46 | 13 | 10 | 12 | 11 | 0 | 11 | 8 | 15 | 42 | 13 | 12 | 20 | 13 | 9 | 0 | 0 | 10 | 0 | 8 | 18 | 0 | 15 | 6 |  | 47
Aluminum (total) | ug/L | CY Chart |  | 107 | 121 | 110 | 101 | 98 | 121 |  | 91 |  | 92 | 92 | 62 | 81 | 85 | 88 |  | 156 | 169 | 911 | 164 | 469 | 222 | 416 | 399 | 259 | 173.5 |  | 224 | 302 | 783 | 392 | 234 | 124 | 242 | 249 | 194 | 184 | 145 | 326 | 308 | 449 | 922 | 202 | 324 | 1020 | 442 | 325 | 200 | 176 | 102 | 148 |  | 47
Aluminum (particulate) | µg/L (Calc) | CY Chart |  | 94 | 62 | 74 | 89 | 90 | 104 | uncalcuable | 84 | uncalcuable | 92 | 86 | 62 | 81 | 85 | 88 | uncalcuable | 156 | 169 | 911 | 153 | 453 | 214 | 416 | 371 | 229 | 144.5 | uncalcuable | 178 | 289 | 773 | 380 | 223 | 124 | 231 | 241 | 179 | 142 | 132 | 314 | 288 | 436 | 913 | 202 | 324 | 1010 | 442 | 317 | 182 | 176 | 87 | 142 | uncalcuable | 47
Ammonia N | mg/L N | CY Chart |  |  | 0.06 | 0.06 |  |  |  |  | 0.08 |  | 0.04 |  | 0 | 0 | 0 | 0 |  | 0.04 | 0.05 | 0.06 | 0.05 | 0.05 | 0.06 | 0.05 | 0.04 | 0.08 | 0.08 | 0.04 | 0.07 | 0.07 | 0.1 | 0.05 | 0.05 | 0.06 | 0.06 | 0.04 | 0.05 | 0.07 | 0.1 | 0.08 | 0.07 | 0.12 | 0.06 | 0.1 | 0.05 | 0.1 | 0.07 | 0.09 | 0.04 | 0.07 | 0.07 | 0 |  | 43
BOD (5-day) | mg/L |  |  | 2.6 | 2.1 | 2 | 2.3 | 2 | 2.1 | 1.5 |  |  | 1.6 |  | 1.5 | 4 |  | 4.2 |  | 5.5 | 3.3 | 2.5 | 1.9 | 2.1 |  | 1.6 | 2.3 |  | 3 |  | 3.6 | 3.9 | 3.8 | 5.2 | 3.3 | 0.5 | 3.2 | 3.2 | 2.7 | 2.7 | 1.3 | 2.4 | 0.9 | 7.2 | 3.5 | 4 | 3.3 | 2.1 | 2.7 | 2.6 | 3.6 | 3.6 | 1.9 |  |  | 42
Bromide | mg/L | CY Chart |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 47
Chlorophyll a | µg/L | CY Chart |  |  | 11 | 6 | 5 | 6 | 5 |  | 7 |  | 4 |  | 12 | 25 |  | 39 | 24 | 21 | 15 | 15 | 11 | 15 | 10 | 17 | 24 | 47 | 50 | 42 | 26 | 40 | 56 | 39 | 43 | 44 | 60 | 54 | 42 | 53 | 44 | 47 | 53 | 47 | 25 | 15 | 2 | 7 | 9 | 10 | 11 | 14 | 11 | 12 |  | 46
Fluoride | mg/L | CY Chart |  | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.21 |  | 0.21 | 0.21 | 0.21 | 0.2 | 0.19 | 0.2 | 0.21 | 0.2 | 0.17 | 0.18 | 0.18 | 0.19 | 0.19 | 0.19 | 0.2 | 0.2 | 0.2 | 0.2 | 0.21 | 0.21 | 0.21 | 0.21 | 0.2 | 0.2 | 0.21 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.21 | 0.21 |  | 50
Iron (dissolved) | mg/L | CY Chart | [5 empty] | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 42
Iron (total) | mg/L | CY Chart | [5 empty] | 0.05 | 0.09 |  | 0.07 |  | 0.07 |  | 0.05 | 0.05 | 0.08 | 0.08 |  | 0.1 | 0.13 | 0.42 | 0.11 | 0.26 | 0.12 | 0.24 | 0.18 | 0.18 | 0.1 | 0.21 | 0.13 | 0.16 | 0.31 | 0.21 | 0.14 | 0.1 | 0.15 | 0.1 | 0.07 | 0.1 | 0.07 | 0.16 | 0.16 | 0.21 | 0.48 | 0.14 | 0.17 |  | 0.26 | 0.17 | 0.09 | 0.08 | 0.03 | 0.07 |  | 42
Manganese (dissolved) | mg/L | CY Chart | [5 empty] | 0.01 | 0.01 |  | 0.02 |  | 0.03 |  | 0.1 | 0.08 | 0.24 | 0.29 |  | 0.28 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0.01 | 0 |  | 0 | 0 | 0 | 0.01 | 0.01 | 0 |  | 42
Manganese(total) | mg/L | CY Chart | [5 empty] | 0.04 | 0.05 |  | 0.08 |  | 0.09 |  | 0.16 | 0.17 | 0.32 | 0.39 |  | 0.42 | 0.11 | 0.09 | 0.04 | 0.05 | 0.04 | 0.05 | 0.05 | 0.06 | 0.07 | 0.09 | 0.08 | 0.1 | 0.11 | 0.1 | 0.09 | 0.06 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.05 | 0.05 | 0.02 | 0.02 |  | 0.02 | 0.02 | 0.02 | 0.02 | 0.01 | 0.02 |  | 42
Nitrate | mg/L | CY Chart |  |  | 0 | 0.07 | 0.07 | 0.08 | 0.11 |  | 0.16 |  | 0.22 | 0.25 | 0.24 | 0.14 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0.04 | 0.03 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 47
Organic N | mg/L | CY Chart |  |  | 0.55 | 0.54 |  |  |  |  | 0.55 |  | 0.41 |  | 0.35 | 0.7 | 0.9 | 0.53 |  | 0.78 | 0.7 | 0.72 | 0.66 | 0.6 | 0.59 | 0.66 | 0.81 | 1.03 | 1.12 | 1.07 | 1.03 | 0.88 | 1.05 | 1.07 | 1.03 | 0.9 | 1 | 1.08 | 1.36 | 1.16 | 1.18 | 1.45 | 1.49 | 1.35 | 1.6 | 0.82 | 0.54 | 0.63 | 0.56 | 0.55 | 0.57 | 0.63 | 0.61 | 0.64 |  | 43
Raw TOC | mg/L C (UV) | CY Chart |  | 8.8 | 9.4 | 8.9 | 8.8 | 8.3 | 8.4 | 8.8 | 8.4 |  | 8.3 | 8.3 | 7.7 | 8.1 | 9.5 | 9.1 | 9 | 9.7 | 7.7 | 8.5 | 7.8 | 8 | 7.6 | 7.7 | 8.9 | 9.1 | 10.6 | 10.2 | 9.1 | 9 | 10.4 | 9.2 | 10.4 | 9.2 | 10.6 | 10.4 | 11.4 | 11 | 11.6 | 11.2 | 12 | 11.8 | 11.5 | 8.2 | 7.4 | 8 | 7 | 7.6 | 7.4 | 7.1 | 7.6 | 7.4 |  | 50
Raw DOC (GF diss) | mg/L C (UV) | CY Chart |  | 8.2 | 8.9 | 8.2 | 8.3 | 7.9 | 8.2 | 7.8 | 8 | 8.1 | 8.1 | 8.2 | 7.5 | 7.1 | 7.7 | 7.6 | 7.6 | 8 | 6.6 | 7 | 6.8 | 6.5 | 6.8 | 6.7 | 7.6 | 7.1 | 8.2 | 7.7 | 7.6 | 7.4 | 7.5 | 7.6 | 7.4 | 7 | 7.6 | 7.4 | 7.2 | 7.8 | 8.4 | 8 | 7.6 | 7.6 | 7.6 | 7 | 6.8 | 6.8 | 6 | 6.7 | 6.6 | 6.3 | 6.6 | 6.4 |  | 51
Org. Carbon (diss @ 254nm) | Abs 10cm | CY Chart |  |  | 0.8937 | 0.8872 | 0.8705 | 0.894 | 0.8801 |  | 0.9084 | 0.8949 | 0.9101 |  | 0.898 | 0.8984 | 0.9723 | 0.8769 | 0.8713 | 0.8891 | 0.6866 | 0.7187 | 0.7262 | 0.7284 | 0.7368 | 0.7456 | 0.7736 | 0.718 | 0.7766 | 0.7854 | 0.8159 | 0.7927 | 0.8064 | 0.7772 | 0.823 | 0.8331 | 0.8284 | 0.8436 | 0.8652 | 0.8885 | 0.8985 | 0.8328 | 0.8235 | 0.8069 | 0.8183 | 0.794 | 1.1294 | 0.8248 | 0.7309 | 0.7482 | 0.7077 | 0.7473 | 0.7542 | 0.7633 |  | 48
UV@254/Raw DOC | ratio | CY Chart |  | -- | 0.10042 | 0.1082 | 0.10488 | 0.11316 | 0.10733 | -- | 0.11355 | 0.11048 | 0.11236 | -- | 0.11973 | 0.12654 | 0.12627 | 0.11538 | 0.11464 | 0.11114 | 0.10403 | 0.10267 | 0.10679 | 0.11206 | 0.10835 | 0.11128 | 0.10179 | 0.10113 | 0.094707 | 0.102 | 0.10736 | 0.10712 | 0.10752 | 0.10226 | 0.11122 | 0.11901 | 0.109 | 0.114 | 0.12017 | 0.11391 | 0.10696 | 0.1041 | 0.10836 | 0.10617 | 0.10767 | 0.11343 | 0.16609 | 0.12129 | 0.12182 | 0.11167 | 0.10723 | 0.11862 | 0.11427 | 0.11927 | -- | 48
Phosphate(ortho) | µg/L P | CY Chart |  |  | 19 |  | 17 |  |  |  | 23 |  | 19 |  | 0 | 8 | 12 | 8 |  | 7 | 4 | 7 | 6 | 6 | 14 | 11 | 6 | 1 | 3 | 3 | 8 | 2 | 4 | 9 | 6 | 6 | 6 | 5 | 9 | 12 | 9 | 11 | 10 | 13 | 16 | 12 | 14 | 18 | 13 | 14 | 10 | 15 | 12 | 13 |  | 43
Phosphate(total) | µg/L P |  |  |  | 45 | 52 | 45 |  |  |  | 46 |  | 40 |  | 40 | 39 | 59 | 66 |  | 75 | 57 | 91 | 60 | 176 | 70 | 153 | 84 | 78 | 80 | 100 | 112 | 86 | 118 | 118 | 106 | 100 | 108 | 118 | 118 | 112 | 96 | 114 | 108 | 112 | 148 | 78 | 58 | 80 | 45 | 56 | 53 | 64 | 50 | 52 |  | 44
Silica (SiO3) | mg/L |  |  |  | 7.4 | 8.3 | 7.73 | 8.34 | 8.54 |  | 8.79 |  | 9.2 | 9.55 | 9.39 | 9.17 | 8.36 | 8.48 | 8.5 | 8.76 | 5.78 | 6.2 | 6.54 | 5.86 | 6.64 | 6.6 | 6.72 | 7.14 | 8.04 | 8.52 | 9.19 | 9 | 9.19 | 9.66 | 10.4 | 10.65 | 11.5 | 11.66 | 12.34 | 11.62 | 11.09 | 11.42 | 11.6 | 12.09 | 11.5 | 11.43 | 10.82 | 9.91 | 10.2 | 10.9 | 9.65 | 10.44 | 11.02 | 11.12 |  | 48
Sulphide | µg/L |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 46
0
0
0
0
0
0
0
0
0
0
0
0
0
PreFM | [55 empty] | 0
TTHM's (total) | µg/L(calc) |  |  | 19 | 27 | 26 | 26 | 18 | 20 | 23 | 20 | uncalcuable | 21 | 22 | 23 | 26 | 30 | 29 | uncalcuable | 35 | 28 | 33 | 37 | 32 | 33 | 36 | 33 | 38 | 43 | 52 | 41 | 47 | 48 | 50 | 47 | 42 | 51 | 45 | 41 | 37 | 38 | 35 | 38 | 37 | 28 | 26 | 20 | 23 | 21 | 20 | 21 | 22 | 23 | 29 | 22 | 50
Chloroform | µg/L |  |  | 12 | 17 | 18 | 18 | 12 | 13 | 15 | 14 |  | 14 | 15 | 16 | 17 | 22 | 20 |  | 23 | 20 | 23 | 25 | 21 | 22 | 24 | 21 | 24 | 28 | 34 | 25 | 32 | 34 | 34 | 33 | 29 | 37 | 32 | 29 | 28 | 27 | 25 | 28 | 27 | 21 | 18 | 14 | 15 | 15 | 14 | 14 | 16 | 15 | 20 | 14 | 50
Bromodichloromethane | µg/L |  |  | 6 | 8 | 7 | 7 | 5 | 6 | 7 | 5 |  | 6 | 6 | 6 | 7 | 7 | 7 |  | 10 | 7 | 8 | 10 | 9 | 9 | 10 | 10 | 11 | 12 | 14 | 12 | 12 | 12 | 13 | 12 | 11 | 12 | 11 | 10 | 8 | 9 | 8 | 9 | 8 | 6 | 7 | 5 | 6 | 5 | 5 | 6 | 5 | 6 | 7 | 6 | 50
Chlorodibromomethane | µg/L |  |  | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 2 | 1 | 2 |  | 2 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 4 | 3 | 3 | 2 | 3 | 2 | 2 | 2 | 2 | 2 | 1 | 2 | 2 | 1 | 2 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 50
Bromoform | µg/L |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50
BIOLOGICAL |  | CY Chart
Blue Green Algae (x10^-3) | per litre |  |  |  | 0 | 0 | 0 | 0 | 0 | 20 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 0 | 26 | 46 | 61 | 69.2 | 409.2 | 1370 | 3400 | 3140 |  | 700 | 680 | 3820 | 1420 | 1270 | 1770 | 5020 | 3500 | 6350 | 8640 | 8780 | 12600 | 13780 | 13620 | 15120 | 6660 | 380 |  | 120 | 60 | 40 | 0 | 60 | 20
Green Algae (x10^-3) | per litre |  |  |  | 1500 | 480 | 380 | 360 | 380 | 820 | 660 |  | 420 | 830 | 2480 | 10760 | 16540 | 15460 | 7760 | 7640 | 2760 | 1800 | 1380 | 980 | 1380 | 1480 | 1260 | 1400 | 1220 |  | 1760 | 700 | 920 | 1280 | 1000 | 1320 | 1800 | 1120 | 700 | 1380 | 940 | 1380 | 980 | 720 | 720 | 540 | 440 |  | 520 | 400 | 580 | 560 | 420 | 640
Diatoms (x10^-3) | per litre |  |  |  | 60 | 40 | 0 | 20 | 20 | 0 | 0 |  | 0 | 0 | 0 | 100 | 380 | 360 | 140 | 100 | 160 | 400 | 280 | 200 | 80 | 460 | 280 | 200 | 160 |  | 1140 | 120 | 240 | 520 | 460 | 1300 | 320 | 180 | 460 | 240 | 200 | 160 | 60 | 180 | 200 | 100 | 120 |  | 100 | 80 | 60 | 80 | 100 | 140
Flagellates (x10^-3) | per litre |  |  |  | 220 | 220 | 140 | 200 | 140 | 100 | 120 |  | 180 | 210 | 1100 | 2140 | 3240 | 1960 | 1640 | 2220 | 2540 | 1300 | 1300 | 2280 | 2680 | 1420 | 900 | 1700 | 2680 |  | 2460 | 3680 | 2420 | 1760 | 4380 | 4420 | 3700 | 2620 | 1980 | 1080 | 420 | 60 | 60 | 120 | 220 | 60 | 100 |  | 800 | 1300 | 1160 | 2040 | 1980 | 2540
Crustaceans | per litre |  |  |  | 10 | 13 | 13 | 20 | 37 | 0 | 17 |  |  | 16 | 60 | 23 | 70 | 110 |  | 103 | 17 | 10 | 27 | 73 | 20 | 107 |  | 67 | 73 |  | 50 | 113 | 70 | 0 | 73 | 83 | 120 | 177 | 300 | 420 | 147 | 63 | 200 | 73 | 7 | 90 | 150 |  | 43 | 13 | 23 | 97 | 27 | 80
Nematodes (x10^-3) | per litre |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
Rotifers (x10^-3) | per litre |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 |  | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 20 | 0 | 0 | 0
Other (x10^-3) | per litre |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
Total Green & B-G | per litre |  |  | uncalcuable | 1500 | 480 | 380 | 360 | 380 | 840 | 660 | uncalcuable | 420 | 830 | 2480 | 10760 | 16540 | 15460 | 7780 | 7660 | 2760 | 1826 | 1426 | 1041 | 1449.2 | 1889.2 | 2630 | 4800 | 4360 | uncalcuable | 2460 | 1380 | 4740 | 2700 | 2270 | 3090 | 6820 | 4620 | 7050 | 10020 | 9720 | 13980 | 14760 | 14340 | 15840 | 7200 | 820 | uncalcuable | 640 | 460 | 620 | 560 | 480 | 660 | uncalcuable
BACTERIOLOGICAL
Total Coliforms | per 100 ml |  |  | 0 | 0 | 5 | 7 | 0 | 2.5 | 0 | 0 |  | 1 | 0 | 2.5 | 0 | 2.5 | 2 | 0 | 12 | 5 | 42 | 5 | 7 | 25 | 5 | 10 | 20 | 0 | 88 | 0 | 250 | 0 | 150 | 0 | 600 | 0 | 375 | 167 | 0 | 200 | 100 | 50 | 33 | 75 | 0 | 12.5 | 25 | 0 | 0 | 12.5 | 5.2 | 1.5 | 20 | 0
Faecal Coliforms | per 100 ml |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 1.25 | 0 | 0 | 0 | 0.5 | 2 | 4 | 0 | 0.5 | 3.8 | 1 | 1 | 0.75 | 1.8 | 4.8 | 2 | 6 | 10.8 | 1.3 | 3 | 16 | 13.2 | 4.7 | 8.8 | 14.5 | 5.5 | 25.2 | 15 | 10 | 2.5 | 2 | 0.8 | 0.25 | 0 | 0 | 0.2 | 0 | 0 | 1
E. coli | per 100 ml
Faecal Streptococci | per 100 ml |  |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 472 | 9 | 0 | 0 | 0 | 11 | 0 | 6 | 7 | 2 | 6 | 4 | 2 | 9 | 30 | 17 | 11 | 51 | 5 | 8 | 26 | 76 | 34 | 29 | 69 | 141 | 89 | 47 | 118 | 83 | 57 | 25 | 10 | 15 | 5 | 6 | 7 | 2
Standard Plate Count | per 1 ml |  |  | 25.8 | 23.6 | 25.7 | 21 | 89.9 | 25.9 | 24 | 26.2 |  | 11.6 | 11.8 | 19.3 | 16.8 | 1610 | 80.2 | 27 | 12 | 38 | 65.2 | 49 | 55 | 36 | 44 | 96 | 100 | 3426 | 435 | 394 | 405 | 405 | 471 | 449 | 350 | 730 | 534 | 838 | 742 | 375 | 333 | 156.4 | 440 | 340 | 233 | 258 | 457 | 216 | 244 |  | 221 | 178 | 128 | 139
CHEMICAL DOSES
Alum | mg/L |  |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 65 | 65 | 65 | 65 | 70 | 72.5 | 73 | 72.5 | 72.5 | 70 | 70 | 65 | 65 | 65 | 65 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 80 | 80 | 90 | 90 | 90 | 80 | 80 | 82 | 82 | 100 | 85 | 85 | 75 | 80 | 60 | 55 | 60 | 55 | 55 | 65
Alum\Raw DOC | ratio | CY Chart |  | 7.3171 | 6.7416 | 7.3171 | 7.2289 | 7.5949 | 7.3171 | 7.6923 | 7.5 | uncalcuable | 8.0247 | 7.9268 | 8.6667 | 9.1549 | 9.0909 | 9.5395 | 9.6053 | 9.0625 | 10.9848 | 10 | 10.2941 | 10 | 9.5588 | 9.7015 | 8.5526 | 9.8592 | 8.5366 | 9.0909 | 9.2105 | 9.4595 | 9.3333 | 9.2105 | 9.4595 | 11.4286 | 10.5263 | 12.1622 | 12.5 | 11.5385 | 9.5238 | 10 | 10.7895 | 10.7895 | 13.1579 | 12.1429 | 12.5 | 11.0294 | 13.3333 | 8.9552 | 8.3333 | 9.5238 | 8.3333 | 8.5938 | uncalcuable
Chlorine-pre | mg/L |  |  | 3.5 | 3.8 | 3.8 | 4.5 | 4.2 | 4 | 4.6 | 5 |  | 5 | 3.7 | 3.6 | 4.33 | 5.5 | 5.5 | 5.5 | 5 | 4.9 | 4.1 | 3.8 | 3.7 | 3.4 | 2.9 | 2.4 | 3.7 | 3.6 | 4.2 | 3.7 | 4.1 | 5.2 | 5.4 | 4.6 | 4.4 | 4.7 | 5 | 5.5 | 5.1 | 4.7 | 4.8 | 4.5 | 3.9 | 3.7 | 2.8 | 1.6 | 1.9 | 2.5 | 2.3 | 3.4 | 3.2 | 3.3 | 3.4 | 3.3 | 0.24281
Chlorine-intermed | mg/L
Chlorine-post | mg/L |  |  | 2001-06-08: 1.2; 2001-06-15: 1.2; 2001-06-22: 1.3; 2001-06-29: 1.2; 2001-07-06: 1.5; 2001-07-13: 1.4; 2001-07-20: 1.6; 2001-07-27: 1.5; 2001-08-03: 1.3; 2001-08-10: 1.2; 2001-08-17: 1; 2001-08-24: 1.3; 2001-08-31: 1.2; 2001-09-07: 1.1; 2001-09-14: 1.2; 2001-09-21: 1.1; 2001-09-28: 1.2; 2001-10-05: 1.2; 2001-10-12: 1.2; 2001-10-19: 1.1; 2001-10-26: 1.3; 2001-11-02: 1.2; 2001-11-09: 1.4; 2001-11-16: 1.5; 2001-11-23: 1.3
Fluoride (Set Point for MJ) | mg/L |  |  | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 |  | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
Powdered Carbon | mg/L
Total Chlorine dose | mg/L (Calc) |  |  | 3.5 | 3.8 | 3.8 | 4.5 | 4.2 | 4 | 4.6 | 5 | -- | 5 | 3.7 | 3.6 | 4.33 | 5.5 | 5.5 | 5.5 | 5 | 4.9 | 4.1 | 3.8 | 3.7 | 3.4 | 4.1 | 3.6 | 5 | 4.8 | 5.7 | 5.1 | 5.7 | 6.7 | 6.7 | 5.8 | 5.4 | 6 | 6.2 | 6.6 | 6.3 | 5.8 | 6 | 5.7 | 5.1 | 4.8 | 4.1 | 2.8 | 3.3 | 4 | 3.6 | 3.4 | 3.2 | 3.3 | 3.4 | 3.3
Date GAC`s ON |  |  |  | 2001-06-01: 2001-05-31
Date GAC`s OFF |  |  |  | 2001-11-23: 2001-11-20
Date Ice ON Lake |  |  |  | 2001-11-30: 2001-11-27
Date Ice OFF Lake |  |  |  | 2001-04-27: 2001-04-27
Date PAC ON |  |  |  | 2001-04-06: 2001-04-03
Date PAC OFF |  |  |  | 2001-05-04: 2001-04-30
Chlorine Residuals Exit Plant (week avg.)
Free Chlorine | mg/L |  |  | 1.12 | 1.15 | 1.11 | 1.12 | 1.08 | 1.05 | 1.14 | 1.07 | 1.05 | 1.08 | 1.04 | 1.05 | 0.975 | 0.98 | 1.05 | 1 | 1.02 |  | 1.05 | 1.04 | 1.05 | 1.05 | 0.96 | 0.95 | 0.98 | 0.96 | 0.93 | 0.97 | 1.01 | 1.01 | 1.05 | 1.04 | 1.08 | 1.1 | 1.07 | 1.04 | 1.12 | 1.05 | 1.13 | 1.07 | 1.1 | 1.1 | 1.08 | 1.11 | 1.11 | 1.05 | 1.11 | 1.14 | 1.19 | 1.15 | 1.16 | 1.18
Combined Chlorine | mg/L |  |  | 0.22 | 0.43 | 0.44 | 0.58 | 0.45 | 0.44 | 0.48 | 0.44 | 0.38 | 0.48 | 0.46 | 0.42 | 0.425 | 0.41 | 0.36 | 0.37 | 0.33 |  | 0.33 | 0.34 | 0.34 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0.06 | 0.09 | 0.09 | 0.08 | 0.09 | 0.08 | 0.1 | 0.12 | 0.12 | 0.12 | 0.14 | 0.12 | 0.13 | 0.12 | 0.12 | 0.14 | 0.13 | 0.12 | 0.15 | 0.26 | 0.3 | 0.29 | 0.31 | 0.33 | 0.3
2001 - BUFFALO POUND WATER QUALITY DATA
CLEAR WELL
Parameters | Units | time axis 2001-01-01 to 2001-12-24
|  |  |  | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to | to
 | time axis 2001-01-05 to 2001-12-28
PHYSICAL
Colour (Apparent) | Pt/Co |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49
Conductivity | µS/cm |  |  | 712 | 717 | 719 | 722 | 726 | 729 | 736 | 746 |  | 756 | 757 | 762 | 744 | 729 | 720 |  | 751 | 597 | 587 | 604 | 607 | 609 | 624 | 616 | 610 | 603 | 600 | 598 | 582 | 564 | 564 | 552 | 536 | 546 | 551 | 551 | 553 | 544 | 546 | 552 | 553 | 568 | 562 | 565 | 566 | 565 | 567 | 574 | 587 | 608 | 619 |  | 49
Diss. Oxygen | mg/L |  |  | 12.5 | 12.6 | 13.1 | 12.3 | 12.6 | 12.4 | 11.8 | 11.5 |  | 12 | 10.6 | 12.3 | 11.8 | 12.5 | 12.1 | 12.5 | 11.6 | 11.4 | 10.7 | 10 | 10.6 | 9.6 | 9.5 | 9.8 | 9.2 | 8.8 | 9 | 8.5 | 8.5 | 8.4 | 8.4 | 8.2 | 8.4 | 9 | 9 | 9.1 | 10 | 9.6 | 10 | 9.4 | 10.9 | 11.3 | 11.7 | 12.5 | 12.6 | 13 | 13.4 | 12.8 | 12.6 | 12.9 | 12.5 | 13.5 | 51
% Sat. Diss. Oxygen | % | CY Chart |  | 92.6612 | 93.1953 | 97.9073 | 92.4812 | 93.9597 | 92.9535 | 89.1912 | 86.2069 | uncalcuable | 90.4295 | 80.7927 | 92.4812 | 91.3313 | 97.8091 | 96.1844 | 101.461 | 96.0265 | 96.5284 | 97.0962 | 97.7517 | 99.344 | 97.0677 | 95.0951 | 101.8711 | 96.0334 | 97.561 | 97.6139 | 95.2915 | 96.0452 | 97.1098 | 95.4545 | 96.4706 | 94.382 | 101.1236 | 99.3377 | 96.5005 | 101.5228 | 95.6175 | 96.2464 | 92.8854 | 96.6312 | 91.7208 | 93.75 | 94.697 | 96.2567 | 96.9426 | 98.5294 | 88.7041 | 119.8858 | 92.4731 | 91.1743 | 99.2647 | 51
Odour (Chlorinated) | T.O.N. | [54 empty] | 0
Odour(Dechlorinated) | T.O.N. | CY Chart |  | 4 | 5 | 4 | 4 |  | 5 |  | 6 |  | 4 |  | 6 | 16 | 23 | 18 | 14 | 12 | 11 | 12 | 10 | 10 | 11 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2 | 2 | 1 | 4 | 3 | 6 | 5 | 5 | 6 | 8 | 5 | 6 | 7 | 6 | 3 | 5 | 5 | 11 | 16 | 12 | 16 |  | 47
PreGAC Odour | T.O.N. |  |  | 2001-06-08: 38; 2001-06-15: 27; 2001-06-22: 85; 2001-06-29: 133; 2001-07-06: 116; 2001-07-13: 90; 2001-07-20: 87; 2001-07-27: 80; 2001-08-03: 115; 2001-08-10: 55; 2001-08-17: 52; 2001-08-24: 82; 2001-08-31: 90; 2001-09-07: 80; 2001-09-14: 93; 2001-09-21: 50; 2001-09-28: 40; 2001-10-05: 37; 2001-10-12: 33; 2001-10-19: 20; 2001-10-26: 23; 2001-11-02: 17; 2001-11-09: 11; 2001-11-16: 15; 2001-11-23: 11 | 25
Odour Removal by Coagulation and Filtration | % |  |  | 66.67% | 68.75% | 66.67% | 71.43% | uncalcuable | 50% | uncalcuable | 66.67% | uncalcuable | 60% | uncalcuable | 57.14% | 54.29% | 58.18% | 90.53% | 86% | 94% | 91.54% | 85.88% | 88.89% | 87.5% | 89% | 55.29% | 82% | 57.5% | 59.08% | 30.12% | 55% | 0% | 13.98% | 8% | 42.11% | 53.57% | 13.68% | 40% | 44.44% | 23.77% | 37.5% | 33.33% | 53.75% | 23.26% | 60% | 23.33% | -6.25% | 42.11% | 31.82% | 35.29% | 59.26% | 0% | 55.56% | 46.67% | uncalcuable | 47
Odour Removal Overall | % |  |  | 66.67% | 68.75% | 66.67% | 71.43% | uncalcuable | 50% | uncalcuable | 66.67% | uncalcuable | 60% | uncalcuable | 57.14% | 54.29% | 58.18% | 90.53% | 86% | 94% | 91.54% | 85.88% | 88.89% | 87.5% | 89% | 100% | 100% | 100% | 100% | 100% | 99.5% | 100% | 98.92% | 98.4% | 97.89% | 99.11% | 95.79% | 98% | 95.83% | 95.9% | 93.75% | 90% | 90% | 88.37% | 88% | 76.67% | 62.5% | 84.21% | 77.27% | 70.59% | 59.26% | 0% | 55.56% | 46.67% | uncalcuable | 47
Particles | per 10 ml |  |  | 122 | 86 |  | 87 | 106 |  |  | 170 |  | 50 | 119 |  | 512 |  | 689 |  | 311 | 95 | 128 | 151.79 | 150 | 255.06 | 564.38 | 477 | 200 | 374 | 369 | 265 | 279 | 524 | 228 | 149 | 116 | 116 | 136 | 122 | 79 | 55 | 78 | 65 | 89 |  | 50 | 48 | 40 | 35 | 87 |  | 138 | 113 | 101 |  | 42
pH | pH units | CY Chart |  | 7.27 | 7.46 | 7.43 | 7.38 | 7.25 | 7.24 | 7.42 | 7.24 |  | 7.4 | 7.1 | 7.26 | 7.28 | 7.2 | 7.41 | 7.46 | 7.43 | 7.25 | 7.32 | 7.32 | 7.3 | 7.27 | 7.58 | 7.34 | 7.41 | 7.45 | 7.64 | 7.36 | 7.39 | 7.39 | 7.44 | 7.33 | 7.26 | 7.19 | 7.08 | 7.14 | 7.25 | 7.19 | 7.25 | 7.19 | 7.26 | 7.3 | 7.31 | 7.18 | 7.2 | 7.08 | 7.33 | 7.43 | 7.14 | 7.33 | 7.3 | 7.3 | 51
Coagulation pH (Channel 1) | pH units |  |  | 7.2 | 7.16 | 7.17 | 7.03 | 7.06 | 7.02 | 7.09 | 7.04 |  | 7.13 | 7.06 | 7.08 | 7.02 |  | 7.02 | 7.07 | 7.09 | 6.98 | 7.05 | 7.03 | 7.06 | 7.09 | 7.1 | 7.13 | 7.12 | 6.98 | 7.25 | 6.94 | 7 | 6.96 | 6.97 | 7.03 | 6.96 | 6.95 | 6.83 | 6.89 | 6.79 | 6.94 | 6.9 | 6.97 | 6.94 | 6.96 | 6.92 | 6.95 | 6.94 | 6.78 | 7.08 | 7.16 | 7.13 | 7.17 | 7.19 |  | 49
SST | mg/L |  |  |  | 0.4 | 0.4 | 0.2 |  | 0.4 |  | 0.5 |  | 0.6 |  | 0.5 | 0.4 |  | 0.2 |  | 0.5 | 0.2 | 0.2 | 0.2 | 0.1 | 0.4 | 0.2 | 0.3 | 0.4 | 0.2 | 0 | 0.2 | 0.2 | 0.3 | 0.4 | 0.5 | 0.3 | 0.4 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.3 | 0.3 | 0.2 | 0.3 | 0.2 | 0.4 | 0.4 | 0.3 | 0.6 | 0.7 | 0.3 |  | 44
SSV | mg/L |  |  |  | 0.1 | 0.2 | 0.2 |  | 0.2 |  | 0.3 |  | 0.2 |  | 0.4 | 0.3 |  | 0.1 |  | 0.5 | 0.2 | 0.1 | 0.2 | 0.3 | 0.7 | 0.1 | 0.2 | 0.2 | 0.2 | 0 | 0.2 | 0.1 | 0.2 | 0.3 | 0.2 | 0.2 | 0.4 | 0.2 | 0.2 | 0.1 | 0.2 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 |  | 44
SSF | mg/L |  |  |  | 0.3 | 0.2 | 0 |  | 0.2 |  | 0.2 |  | 0.4 |  | 0.1 | 0.1 |  | 0.1 |  | 0 | 0 | 0.1 | 0 | 0.1 | 0.3 | 0.1 | 0.1 | 0.2 | 0 | 0 | 20.9 | 0.1 | 0.1 | 0.1 | 0.3 | 0.1 | 0 | 0 | 0.1 | 0.2 | 0.1 | 0 | 0.1 | 0.1 | 0.1 | 0 | 0.1 | 0 | 0.2 | 0.1 | 0 | 0.3 | 0.4 | 0.1 |  | 44
Temperature | ° C |  |  | 2.9 | 2.8 | 3.2 | 3.4 | 3.1 | 3.3 | 3.6 | 3.3 |  | 3.5 | 3.9 | 3.4 | 4.5 | 4.9 | 5.5 | 6.3 | 7.1 | 8 | 10.9 | 14.2 | 12.3 | 15.8 | 15.3 | 17.1 | 17.3 | 20.3 | 19.2 | 20.9 | 21.3 | 22.5 | 21.6 | 23.4 | 21 | 21 | 20.1 | 18.1 | 16 | 15.1 | 13.5 | 14.7 | 9.9 | 6.3 | 5.8 | 3.7 | 4 | 3.1 | 2.6 | 0.5 | 13 | 1.7 | 2.3 | 2.6 | 51
Turbidity | NTU |  |  | 0.08 | 0.14 | 0.08 | 0.08 | 0.09 | 0.08 | 0.07 | 0.07 |  | 0.07 | 0.1 | 0.08 | 0.11 | 0.07 | 0.08 | 0.08 | 0.11 | 0.07 | 0.08 | 0.08 | 0.06 | 0.06 | 0.08 | 0.08 | 0.08 | 0.1 | 0.12 | 0.1 | 0.09 | 0.12 | 0.12 | 0.1 | 0.09 | 0.09 | 0.09 | 0.1 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.08 | 0.1 | 0.06 | 0.07 | 0.12 | 0.13 | 0.15 | 0.15 | 0.15 | 51
Dissolved Solids | mg/L(calc) |  |  | uncalcuable | 550.65 | 560.33 | 558.26 | 566.8 | 567.51 | uncalcuable | 574.28 | #VALUE! | 590.25 | 590.59 | 582.3 | 581.16 | 561.46 | 554.36 | 568.9 | 584 | 448.98 | 444.59 | 453.89 | 455.03 | 463.13 | 476.22 | 471.36 | 463 | 447.84 | uncalcuable | 445.2 | 433.32 | 414.71 | 0 | 401.46 | 401.75 | 401.98 | 399.38 | 405.44 | 404.19 | 402.99 | 404.79 | 408.06 | 410.16 | 418.55 | 417.91 | 416.66 | 422.8 | 420.68 | 427.41 | 430.97 | 449.91 | 462.07 | 473.73 | #VALUE! | 47
Particle Log Removal | (calc) |  |  | 1.9523 | 2.1171 | uncalcuable | 2.0474 | 1.9772 | uncalcuable | uncalcuable | 1.9119 | uncalcuable | 2.4385 | 2.1787 | uncalcuable | 1.9766 | uncalcuable | 1.9215 | uncalcuable | 2.1528 | 2.639 | 2.6567 | 2.5593 | 2.5683 | 2.3593 | 1.8705 | 2.0377 | 2.4055 | 2.1696 | 2.2348 | 2.1135 | 2.2437 | 2.047 | 2.4793 | 2.5601 | 2.5655 | 2.5433 | 2.3941 | 2.4892 | 2.5797 | 2.962 | 2.7076 | 2.8448 | 2.9309 | uncalcuable | 2.7659 | 2.9306 | 3.128 | 3.0246 | 2.5325 | uncalcuable | 1.9901 | 2.1104 | 2.2145 | uncalcuable | 42
Turbidity Log Removal | (calc) |  |  | 1.4717 | 1.2268 | 1.4065 | 1.3711 | 1.349 | 1.4529 | 1.4494 | 1.4993 | uncalcuable | 1.4559 | 1.316 | 1.3248 | 1.3334 | 1.7677 | 1.688 | 1.7709 | 1.706 | 1.8953 | 2.224 | 1.769 | 2.2109 | 1.9654 | 2.1012 | 2.1343 | 2.2928 | 2.1239 | 1.8884 | 1.9469 | 1.9654 | 2.0447 | 2.0762 | 2.0899 | 2.0586 | 1.8952 | 2.2333 | 2.2041 | 1.8381 | 1.7659 | 1.9434 | 1.9601 | 2.0271 | 2.3268 | 1.8203 | 1.8779 | 2.2833 | 2.1357 | 1.9402 | 1.4246 | 1.3953 | 1.0887 | 1.2818 | 1.5366 | 51
Langelier Index (RTW) | pH units (calc) | CY Chart |  |  | -0.27356 | -0.2908 | -0.33242 | -0.45935 | -0.46609 |  | -0.4503 |  | -0.26144 | -0.55717 | -0.40662 | -0.36134 | -0.47728 | -0.27252 | -0.18518 | -0.17389 | -0.54633 | -0.469 | -0.38511 | -0.42625 | -0.3819 | -0.056593 | -0.28601 | -0.2537 | -0.23257 |  | -0.31336 | -0.32522 | -0.3653 | -0.089328 | -0.43035 | -0.49949 | -0.61337 | -0.76268 | -0.71966 | -0.64514 | -0.69211 | -0.63408 | -0.66649 | -0.64542 | -0.6638 | -0.64596 | -0.79916 | -0.73827 | -0.86579 | -0.59455 | -0.50619 | -0.56405 | -0.5265 | -0.52274 |  | 47
0
MAJOR CONSTITUENTS | [55 empty] | 0
0
Alkalinity(p) | mg/L CaCO3 | CY Chart |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 50
Alkalinity(total) | mg/L CaCO3 | CY Chart |  | 166 | 169 | 172 | 171 | 172 | 172 | 174 | 176 |  | 182 | 181 | 180 | 180 | 167 | 166 | 171 | 178 | 130 | 131 | 131 | 131 | 138 | 141 | 138 | 130 | 121 | 118 | 121 | 115 | 107 | 112 | 102 | 101 | 100 | 94 | 97 | 96 | 102 | 105 | 105 | 109 | 107 | 111 | 114 | 119 | 121 | 130 | 135 | 141 | 145 | 151 |  | 50
Bicarbonate | mg/L | CY Chart |  | 202 | 206 | 210 | 208 | 210 | 210 | 212 | 214 |  | 222 | 221 | 219 | 219 | 204 | 202 | 209 | 217 | 158 | 160 | 160 | 160 | 168 | 172 | 168 | 158 | 147 | 144 | 147 | 140 | 130 | 136 | 124 | 123 | 122 | 114 | 118 | 117 | 124 | 128 | 128 | 133 | 130 | 135 | 139 | 145 | 147 | 158 | 165 | 172 | 177 | 184 |  | 50
Carbonate | mg/L | CY Chart |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 50
Calcium | mg/L | CY Chart |  |  | 60 | 60 | 61 | 62 | 62 |  | 63 |  | 65 | 65 | 65 | 66 | 64 | 62 | 64 | 66 | 53 | 48 | 52 | 53 | 53 | 55 | 54 | 52 | 48 | 48 | 48 | 45 | 42 | 42 | 42 | 46 | 42 | 42 | 42 | 42 | 42 | 43 | 44 | 45 | 46 | 46 | 46 | 48 | 48 | 48 | 49 | 50 | 53 | 54 |  | 48
Magnesium | mg/L | CY Chart |  |  | 26 | 27 | 27 | 27 | 27 |  | 27 |  | 28 | 28 | 27 | 26 | 26 | 26 | 27 | 28 | 20 | 19 | 20 | 21 | 21 | 21 | 21 | 20 | 20 | 21 | 20 | 21 | 20 | 20 | 20 | 17 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 22 | 23 |  | 48
Hardness (total) | mg/L CaCO3 | CY Chart |  |  | 259 | 261 | 262 | 265 | 265 |  | 271 |  | 277 | 277 | 276 | 274 | 268 | 262 | 270 | 279 | 214 | 200 | 212 | 217 | 219 | 222 | 221 | 210 | 202 | 206 | 204 | 199 | 189 | 188 | 186 | 185 | 188 | 186 | 186 | 187 | 188 | 189 | 192 | 194 | 197 | 197 | 199 | 200 | 201 | 202 | 205 | 214 | 222 | 227 |  | 48
Sodium | mg/L | CY Chart |  |  | 53 | 54 | 54 | 54 | 54 |  | 54 |  | 55 | 56 | 54 | 54 | 54 | 53 | 52 | 55 | 43 | 43 | 44 | 44 | 44 | 45 | 45 | 46 | 46 |  | 45 | 45 | 43 | 42 | 41 | 41 | 41 | 40 | 42 | 40 | 39 | 38 | 39 | 38 | 39 | 39 | 38 | 39 | 38 | 39 | 38 | 40 | 41 | 42 |  | 47
Potassium | mg/L | CY Chart |  |  | 6.4 | 6.1 | 6 | 6.9 | 7.6 |  | 6.3 |  | 5.5 | 5.4 | 5.7 | 5.5 | 5.7 | 5.2 | 5.3 | 5.7 | 4.4 | 4.6 | 4.7 | 5 | 4.8 | 4.9 | 5 | 5.2 | 5.2 |  | 5.1 | 4.9 | 4.9 | 4.8 | 4.7 | 4.6 | 4.5 | 4.6 | 4.4 | 4.4 | 4.4 | 4.4 | 4.2 | 4.3 | 4.2 | 4.2 | 4 | 4 | 4 | 4 | 4 | 4.1 | 4.2 | 4.2 |  | 47
Sulphate | mg/L | CY Chart |  |  | 175 | 178 | 177 | 181 | 181 |  | 184 |  | 188 | 188 | 185 | 184 | 181 | 179 | 185 | 185 | 150 | 150 | 153 | 152 | 152 | 157 | 157 | 159 | 158 |  | 156 | 153 | 149 | 150 | 145 | 145 | 146 | 152 | 152 | 153 | 146 | 145 | 147 | 144 | 153 | 148 | 146 | 142 | 140 | 135 | 132 | 140 | 141 | 142 |  | 47
Chloride | mg/L | CY Chart |  |  | 16.8 | 17.3 | 17.5 | 17.8 | 17.7 |  | 17.8 |  | 17.9 | 18.2 | 17.4 | 17.6 | 18.3 | 19 | 18.9 | 18.9 | 15.1 | 14.6 | 14.5 | 14.7 | 14.6 | 15 | 14.9 | 16.1 | 16.1 |  | 16.2 | 16.3 | 17.2 | 17.3 | 15.4 | 15.2 | 16 | 16.1 | 15.9 | 16.4 | 15.5 | 15.7 | 15.1 | 14.7 | 15.5 | 15 | 13.5 | 14 | 13.6 | 13.4 | 13.6 | 13.8 | 14.1 | 14.4 |  | 47
0
TRACE CONSTITUENTS | [55 empty] | 0
0
CLEARWELL | [55 empty] | 0
Aluminum (dissolved 0.45µ) | µg/L Chart | CY Chart |  | 59 | 10 | 54 | 56 | 61 | 114 |  | 59 |  | 48 | 58 | 45 | 46 | 22 | 31 |  | 35 | 11 | 20 | 22 | 32 | 22 | 18 | 17 | 23 | 53 |  | 65 | 32 | 14 | 14 | 16 | 12 | 9 | 9 | 8 | 6 | 6 | 7 | 9 | 23 | 0 | 0 | 0 | 6 | 8 | 9 | 52 | 56 | 61 | 54 |  | 47
Aluminum (total) | µg/L Chart | CY Chart |  | 91 | 87 | 88 | 77 | 144 |  |  | 100 |  | 80 | 82 | 65 | 71 | 45 | 43 |  | 52 | 21 | 21 | 33 | 28 | 29 | 20 | 23 | 42 | 56 |  | 91 | 29 | 17 | 15 | 20 | 12 | 13 | 11 | 15 | 10 | 9 | 10 | 19 | 10 | 8 | 6 | 8 | 13 | 14 | 18 | 98 | 130 | 167 | 107 | 58 | 47
Aluminum (total 12 mo avg) | µg/L | [54 empty] | 0
Aluminum (particulate) | µg/L (Calc) | CY Chart |  | 32 | 77 | 34 | 21 | 83 | uncalcuable | uncalcuable | 41 | uncalcuable | 32 | 24 | 20 | 25 | 23 | 12 | uncalcuable | 17 | 10 | 1 | 11 | -4 | 7 | 2 | 6 | 19 | 3 | uncalcuable | 26 | -3 | 3 | 1 | 4 | 0 | 4 | 2 | 7 | 4 | 3 | 3 | 10 | -13 | 8 | 6 | 8 | 7 | 6 | 9 | 46 | 74 | 106 | 53 | uncalcuable | 46
Mixed Media Filter 1 | [55 empty] | 0
Aluminum (total) | µg/L | CY Chart |  | 131 | 125 | 130 | 122 | 167 | 130 |  | 136 |  | 68 | 127 | 100 | [6 empty] | 54 | 56 | 35 | 29 | 38 | 37 | 44 | 49 |  | 98 | 56 | 44 | 44 | 49 |  | 49 | 27 | 26 | 26 |  |  | 35 | 102 | 44 | 38 | 86 | 54 | 76 | 69 | 98 | 107 | 207 | 121 |  | 39
Mixed Media Filter 12 | [55 empty] | 0
Aluminum (total) | µg/L | CY Chart |  | 82 | 76 | 85 | 97 | 74 | 76 |  | 91 |  | 52 | 60 | 81 | 55 | 32 |  |  | 30 | 11 | 20 | 22 | 24 | 28 | 22 | 31 |  | 38 |  | 143 | 58 | 53 | 34 | 38 | 28 | 31 | 28 | 25 | 22 | 28 | 24 | 26 | 36 | 35 | 40 | 44 | 45 | 57 | 46 | 59 | 84 | 59 | 55 |  | 45
PreGAC | [55 empty] | 0
Aluminum (dissolved) | µg/L | CY Chart |  | 2001-06-08: 21; 2001-06-15: 27; 2001-06-22: 42; 2001-06-29: 64; 2001-07-13: 120; 2001-07-20: 42; 2001-07-27: 38; 2001-08-03: 28; 2001-08-10: 33; 2001-08-17: 24; 2001-08-24: 26; 2001-08-31: 19; 2001-09-07: 18; 2001-09-14: 18; 2001-09-21: 22; 2001-09-28: 19; 2001-10-05: 22; 2001-10-12: 28; 2001-10-19: 31; 2001-10-26: 24; 2001-11-02: 41; 2001-11-09: 35; 2001-11-16: 42; 2001-11-23: 46 | 24
Aluminum (total) | µg/L Chart | CY Chart |  | 2001-06-08: 22; 2001-06-15: 35; 2001-06-22: 50; 2001-06-29: 60; 2001-07-13: 131; 2001-07-20: 53; 2001-07-27: 41; 2001-08-03: 31; 2001-08-10: 37; 2001-08-17: 27; 2001-08-24: 31; 2001-08-31: 30; 2001-09-07: 28; 2001-09-14: 23; 2001-09-21: 27; 2001-09-28: 28; 2001-10-05: 28; 2001-10-12: 131; 2001-10-19: 30; 2001-10-26: 31; 2001-11-02: 50; 2001-11-09: 44; 2001-11-16: 64; 2001-11-23: 68 | 24
CW or PreGAC Al (total) | µg/L | CY Chart |  | 91 | 87 | 88 | 77 | 144 | uncalcuable | uncalcuable | 100 | uncalcuable | 80 | 82 | 65 | 71 | 45 | 43 | uncalcuable | 52 | 21 | 21 | 33 | 28 | 29 | 22 | 35 | 50 | 60 | uncalcuable | 131 | 53 | 41 | 31 | 37 | 27 | 31 | 30 | 28 | 23 | 27 | 28 | 28 | 131 | 30 | 31 | 50 | 44 | 64 | 68 | 98 | 130 | 167 | 107 | 58 | 47
Ammonia N | mg/L N | CY Chart |  |  | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0.06 | 0.04 | 0.04 | 0 | 0.06 | 0.06 | 0 | 0 | 0.05 | 0.07 | 0.05 | 0.05 | 0.05 | 0.1 | 0.04 | 0.04 | 0.04 | 0.03 | 0.04 | 0.04 | 0.06 | 0.04 | 0.09 | 0.09 | 0.13 | 0.06 | 0.07 | 0.06 | 0.05 | 0.06 | 0.09 | 0.07 | 0.05 | 0.07 | 0.04 |  | 43
Bromide | mg/L | CY Chart |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 47
Fluoride | mg/L | CY Chart |  | 0.13 | 0.14 | 0.13 | 0.14 | 0.13 | 0.13 | 0.14 | 0.14 |  | 0.15 | 0.13 | 0.14 | 0.14 | 0.12 | 0.12 | 0.13 | 0.13 | 0.1 | 0.11 | 0.11 | 0.12 | 0.12 | 0.12 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.14 | 0.14 | 0.13 | 0.14 | 0.12 | 0.12 | 0.11 | 0.12 | 0.11 | 0.15 | 0.12 | 0.15 | 0.15 | 0.13 | 0.12 | 0.1 | 0.13 | 0.12 | 0.12 | 0.13 | 0.14 | 0.15 | 0.14 |  | 50
Fluoride (actual MJ dose) | mg/L (wk avg) | CY Chart |  | 0.93 | 1.08 | 0.84 | 0.91 | 1.09 | 0.89 | 0.94 | 1.07 |  | 1.01 | 0.91 | 1.02 | 0.98 | 0.97 | 0.91 | 1.05 | 1.03 | 0.9 | 1.01 | 1.03 | 1.15 | 1.08 | 1.06 | 1.17 | 1.13 | 1.13 | 1.14 | 1.01 | 0.78 | 1.04 | 0.95 | 1.06 | 1.03 | 1.04 | 1.04 | 1.08 | 1.02 | 0.99 | 0.94 | 0.97 | 1.02 | 1.01 | 1 | 1.06 | 1.04 | 1.07 | 1.07 | 1.01 | 1.02 | 1 | 1.2 | 1.04 | 51
Iron (dissolved) | mg/L | CY Chart | [5 empty] | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 42
Iron (total) | mg/L | CY Chart | [5 empty] | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 42
Manganese (dissolved) | mg/L | CY Chart | [5 empty] | 0 | 0 |  | 0 |  | 0 |  | 0.01 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 42
Manganese (total) | mg/L | CY Chart | [5 empty] | 0 | 0 |  | 0 |  | 0 |  | 0.01 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 42
Nitrate | mg/L N | CY Chart |  |  | 0.05 | 0.06 | 0.07 | 0.09 | 0.12 |  | 0.15 |  | 0.21 | 0.22 | 0.23 | 0.14 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0.03 | 0.03 | 0.04 | 0.03 | 0.03 | 0.04 | 0.04 | 0.03 | 0.03 | 0.03 | 0.03 | 0.02 | 0.02 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 |  | 47
Organic N | mg/L N | CY Chart |  |  | 0.32 | 0.23 |  |  |  |  | 0.24 |  | 0.15 |  | 0.2 | 0.26 | 0.36 | 0.26 |  | 0.22 | 0.13 | 0.2 | 0.21 | 0.29 | 0.31 | 0.06 | 0.05 | 0.06 | 0.08 | 0.05 | 0.11 | 0.07 | 0.08 | 0.06 | 0.09 | 0.09 | 0.09 | 0.12 | 0.22 | 0.16 | 0.21 | 0.21 | 0.26 | 0.21 | 0.17 | 0.16 | 0.19 | 0.2 | 0.2 | 0.23 | 0.25 | 0.3 | 0.26 | 0.22 |  | 43
CW TOC | mg/L C(UV) | CY Chart |  | 5.3 | 5.6 | 5.4 | 5.5 | 5.3 | 5.5 | 5.5 | 5.5 |  | 5.6 | 5.5 | 5.4 | 5.3 | 5.3 | 4.6 | 4.9 | 5.2 | 3.3 | 4 | 4.2 | 4.1 | 4.4 | 1.1 | 1 | 1 | 1.3 | 1.4 | 1.7 | 1.6 | 2 | 2 | 2.5 | 2.1 | 2.4 | 2.5 | 2.5 | 2.5 | 3 | 3.1 | 3.3 | 3.1 | 2.8 | 2.8 | 2.9 | 3.1 | 3.2 | 3.6 | 4.3 | 4.2 | 4.4 | 4.4 |  | 50
CW DOC (GF diss) | mg/L C(UV) | CY Chart |  | 5.3 | 5.5 | 5.4 | 5.4 | 5.3 | 5.4 | 5.6 | 5.5 | 5.5 | 5.6 | 5.4 | 5.4 | 5.2 | 5.3 | 4.4 | 4.9 | 5 | 3.3 | 4.1 | 4.3 | 4.1 | 4.5 | 1.1 | 1 | 1 | 1.2 | 1.4 | 1.6 | 1.6 | 2.1 | 2 | 2.2 | 2.2 | 2.4 | 2.4 | 2.5 | 2.6 | 3.1 | 3.2 | 3.2 | 3.2 | 2.8 | 2.7 | 2.9 | 3.2 | 3.2 | 3.6 | 4.4 | 4.1 | 4.3 | 4.4 |  | 51
PreGAC DOC (GF diss) | mg/L C(UV) | CY Chart |  | 2001-06-08: 4.3; 2001-06-15: 4.6; 2001-06-22: 4.5; 2001-06-29: 4.7; 2001-07-06: 4.8; 2001-07-13: 4.6; 2001-07-20: 4.4; 2001-07-27: 4.8; 2001-08-03: 4.3; 2001-08-10: 4.6; 2001-08-17: 4; 2001-08-24: 4.4; 2001-08-31: 4.3; 2001-09-07: 4; 2001-09-14: 4.3; 2001-09-21: 4.9; 2001-09-28: 4.9; 2001-10-05: 4.8; 2001-10-12: 4.8; 2001-10-19: 4.1; 2001-10-26: 4.3; 2001-11-02: 4; 2001-11-09: 4.2; 2001-11-16: 3.9; 2001-11-23: 4.2 | 25
DOC Removal by Coagulation & Filtration | % Removal | CY Chart |  | 35.37% | 38.2% | 34.15% | 34.94% | 32.91% | 34.15% | 28.21% | 31.25% | 32.1% | 30.86% | 34.15% | 28% | 26.76% | 31.17% | 42.11% | 35.53% | 37.5% | 50% | 41.43% | 36.76% | 36.92% | 33.82% | 35.82% | 39.47% | 36.62% | 42.68% | 37.66% | 39.47% | 40.54% | 36% | 43.42% | 37.84% | 42.86% | 42.11% | 41.89% | 44.44% | 44.87% | 41.67% | 38.75% | 36.84% | 36.84% | 46.05% | 38.57% | 41.18% | 38.24% | 35% | 37.31% | 33.33% | 34.92% | 34.85% | 31.25% | uncalcuable | 51
DOC Removal by GAC Filtration | % Removal | CY Chart |  | uncalcuable | uncalcuable | uncalcuable | uncalcuable | uncalcuable | uncalcuable | uncalcuable | uncalcuable | uncalcuable | uncalcuable | uncalcuable | uncalcuable | uncalcuable | uncalcuable | uncalcuable | uncalcuable | uncalcuable | uncalcuable | uncalcuable | uncalcuable | uncalcuable | uncalcuable | 74.42% | 78.26% | 77.78% | 74.47% | 70.83% | 65.22% | 63.64% | 56.25% | 53.49% | 52.17% | 45% | 45.45% | 44.19% | 37.5% | 39.53% | 36.73% | 34.69% | 33.33% | 33.33% | 31.71% | 37.21% | 27.5% | 23.81% | 17.95% | 14.29% | uncalcuable | uncalcuable | uncalcuable | uncalcuable | uncalcuable | 25
Total DOC (% Removal) | % Removal | CY Chart |  | 35.37% | 38.2% | 34.15% | 34.94% | 32.91% | 34.15% | 28.21% | 31.25% | 32.1% | 30.86% | 34.15% | 28% | 26.76% | 31.17% | 42.11% | 35.53% | 37.5% | 50% | 41.43% | 36.76% | 36.92% | 33.82% | 83.58% | 86.84% | 85.92% | 85.37% | 81.82% | 78.95% | 78.38% | 72% | 73.68% | 70.27% | 68.57% | 68.42% | 67.57% | 65.28% | 66.67% | 63.1% | 60% | 57.89% | 57.89% | 63.16% | 61.43% | 57.35% | 52.94% | 46.67% | 46.27% | 33.33% | 34.92% | 34.85% | 31.25% | uncalcuable | 51
CW Organic Carbon (diss @ 254nm) | Abs 10cm | CY Chart |  |  | 0.5351 | 0.5675 | 0.5288 | 0.5512 | 0.5476 |  | 0.5572 | 0.5518 | 0.5704 | 0.54 | 0.5565 | 0.5514 | 0.5737 | 0.4177 | 0.4644 | 0.4724 | 0.2836 | 0.3865 | 0.3885 | 0.3935 | 0.404 | 0.0192 | 0.0317 | 0.0019 | 0.0205 | 0.03 | 0.0757 | 0.059 | 0.0735 | 0.0732 | 0.1177 | 0.125 | 0.1363 | 0.1311 | 0.1598 | 0.1463 | 0.2036 | 0.1785 | 0.1963 | 0.1832 | 0.175 | 0.161 | 0.196 | 0.2153 | 0.2386 | 0.2608 | 0.4166 | 0.4155 | 0.4382 | 0.4454 |  | 49
UV@254/CW DOC | ratio | CY Chart |  | uncalcuable | 0.097291 | 0.10509 | 0.097926 | 0.104 | 0.10141 | uncalcuable | 0.10131 | 0.10033 | 0.10186 | 0.1 | 0.10306 | 0.10604 | 0.10825 | 0.094932 | 0.094776 | 0.09448 | 0.085939 | 0.094268 | 0.090349 | 0.095976 | 0.089778 | 0.017455 | 0.0317 | 0.0019 | 0.017083 | 0.021429 | 0.047313 | 0.036875 | 0.035 | 0.0366 | 0.0535 | 0.056818 | 0.056792 | 0.054625 | 0.06392 | 0.056269 | 0.065677 | 0.055781 | 0.061344 | 0.05725 | 0.0625 | 0.05963 | 0.067586 | 0.067281 | 0.074563 | 0.072444 | 0.094682 | 0.10134 | 0.10191 | 0.10123 | uncalcuable | 49
PreGAC Organic Carbon (diss @ 254nm) | Abs 10cm | CY Chart |  | 2001-06-08: 0.4217; 2001-06-15: 0.4376; 2001-06-22: 0.3913; 2001-06-29: 0.4029; 2001-07-06: 0.4197; 2001-07-13: 0.4415; 2001-07-20: 0.42; 2001-07-27: 0.4387; 2001-08-03: 0.4194; 2001-08-10: 0.4332; 2001-08-17: 0.4636; 2001-08-24: 0.4214; 2001-08-31: 0.4094; 2001-09-07: 0.4188; 2001-09-14: 0.415; 2001-09-21: 0.4285; 2001-09-28: 0.4276; 2001-10-05: 0.4125; 2001-10-12: 0.4062; 2001-10-19: 0.3854; 2001-10-26: 0.385; 2001-11-02: 0.3983; 2001-11-09: 0.4045; 2001-11-16: 0.3943; 2001-11-23: 0.4087 | 25
Phosphate(ortho) | µg/L P | CY Chart |  |  | 6 |  | 4 |  |  |  | 5 |  | 6 |  | 0 | 6 | 6 | 0 |  | 4 | 0 | 2 | 2 | 4 | 0 | 44 | 16 | 15 | 9 | 9 | 7 | 4 | 7 | 8 | 5 | 2 | 3 | 5 | 7 | 4 | 7 | 3 | 4 | 6 | 4 | 3 | 3 | 5 | 7 | 4 | 0 | 5 | 0 | 2 |  | 43
Phosphate(total) | µg/L P |  |  |  | 9 | 17 | 11 |  |  |  | 9 |  | 9 |  | 9 | 10 | 8 | 10 |  | 8 | 4 | 5 | 6 | 7 | 5 | 50 | 20 | 14 | 14 | 14 | 21 | 4 | 12 | 9 | 7 | 8 | 8 | 9 | 6 | 6 | 5 | 4 | 7 | 5 | 4 | 5 | 3 | 4 | 5 | 5 | 4 | 6 | 4 | 10 |  | 44
Silica (SiO3) | mg/L |  |  |  | 7.45 | 7.93 | 7.76 | 8.1 | 8.21 |  | 8.18 |  | 8.85 | 8.99 | 9.2 | 9.06 | 8.46 | 8.16 | 7.7 | 8.4 | 5.48 | 5.39 | 5.69 | 5.33 | 5.73 | 6.32 | 6.46 | 6.7 | 7.54 | 7.78 | 7.9 | 8.12 | 8.61 | 8.89 | 9.36 | 9.95 | 10.48 | 10.68 | 11.14 | 11.39 | 12.09 | 10.69 | 10.76 | 11.16 | 10.85 | 10.71 | 10.16 | 10.8 | 10.08 | 10.01 | 9.37 | 10.01 | 9.77 | 10.13 |  | 48
Sulphide | µg/L |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 46
0
CLEARWELL
TTHM's (total) | µg/L(calc) |  |  | 30 | 36 | 35 | 36 | 30 | 29 | 33 | 31 | uncalcuable | 34 | 37 | 23 | 26 | 38 | 26 | uncalcuable | 36 | 23 | 40 | 44 | 39 | 42 | uncalcuable | uncalcuable | 1 | 1 | 2 | 5 | 7 | 14 | 21 | 38 | 44 | 49 | 52 | 48 | 46 | 48 | 45 | 47 | 43 | 39 | 36 | 35 | 32 | 31 | 33 | 25 | 27 | 28 | 30 | 28 | 48
Chloroform | µg/L |  |  | 19 | 22 | 22 | 22 | 19 | 17 | 20 | 19 |  | 21 | 22 | 16 | 17 | 25 | 16 |  | 23 | 16 | 27 | 28 | 25 | 27 | 0 | 0 | 1 | 1 | 2 | 5 | 7 | 13 | 19 | 34 | 40 | 43 | 42 | 38 | 35 | 37 | 34 | 33 | 32 | 29 | 26 | 25 | 23 | 22 | 24 | 18 | 19 | 19 | 20 | 19 | 50
Bromodichloromethane | µg/L |  |  | 9 | 12 | 11 | 12 | 9 | 10 | 11 | 10 |  | 11 | 12 | 6 | 7 | 11 | 8 |  | 11 | 6 | 11 | 13 | 12 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 3 | 4 | 6 | 9 | 9 | 9 | 10 | 10 | 11 | 10 | 9 | 9 | 9 | 8 | 8 | 8 | 6 | 6 | 7 | 8 | 7 | 50
Chlorodibromomethane | µg/L |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 3 | 1 | 2 | 2 | 2 |  | 2 | 1 | 2 | 3 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 50
Bromoform | µg/L |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50
CHANNEL
TTHM's (total) | µg/L(calc) |  |  | 28 | 34 | 31 | 34 | 26 | 29 | 35 | 28 | uncalcuable | 30 | 31 | 29 | 31 | 34 | 27 | uncalcuable | 35 | 21 | 38 | 40 | 34 | 38 | 40 | 38 | 43 | 45 | 56 | 45 | 51 | 58 | 55 | 54 | 50 | 51 | 51 | 48 | 40 | 44 | 39 | 38 | 36 | 35 | 34 | 24 | 27 | 20 | 23 | 26 | 24 | 25 | 26 | 27 | 50
Chloroform | µg/L |  |  | 17 | 21 | 19 | 21 | 16 | 16 | 20 | 18 |  | 18 | 19 | 18 | 20 | 23 | 18 |  | 19 | 15 | 26 | 25 | 22 | 24 | 26 | 23 | 27 | 29 | 36 | 29 | 34 | 40 | 38 | 38 | 35 | 37 | 36 | 34 | 29 | 32 | 29 | 28 | 25 | 24 | 24 | 17 | 18 | 14 | 15 | 19 | 16 | 16 | 18 | 18 | 50
Bromodichloromethane | µg/L |  |  | 9 | 11 | 10 | 11 | 8 | 11 | 13 | 8 |  | 10 | 10 | 9 | 9 | 9 | 8 |  | 13 | 5 | 10 | 12 | 10 | 12 | 12 | 12 | 13 | 13 | 16 | 13 | 14 | 15 | 14 | 14 | 13 | 12 | 13 | 12 | 9 | 10 | 9 | 9 | 9 | 9 | 8 | 6 | 7 | 5 | 6 | 6 | 6 | 7 | 6 | 7 | 50
Chlorodibromomethane | µg/L |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 1 |  | 3 | 1 | 2 | 3 | 2 | 2 | 2 | 3 | 3 | 3 | 4 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 2 | 2 | 2 | 1 | 2 | 1 | 2 | 1 | 2 | 2 | 2 | 2 | 50
Bromoform | µg/L |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50
PreGAC
TTHM's (total) | µg/L(calc) |  |  | uncalcuable | uncalcuable | uncalcuable | uncalcuable | uncalcuable | uncalcuable | uncalcuable | uncalcuable | uncalcuable | uncalcuable | uncalcuable | uncalcuable | uncalcuable | uncalcuable | uncalcuable | uncalcuable | uncalcuable | uncalcuable | uncalcuable | uncalcuable | uncalcuable | uncalcuable | 40 | 32 | 43 | 46 | 59 | 45 | 51 | 58 | 56 | 56 | 54 | 55 | 52 | 48 | 40 | 43 | 42 | 39 | 41 | 37 | 36 | 23 | 30 | 20 | 23 | uncalcuable | uncalcuable | uncalcuable | uncalcuable | uncalcuable | 25
Chloroform | µg/L |  |  | 2001-06-08: 25; 2001-06-15: 20; 2001-06-22: 27; 2001-06-29: 29; 2001-07-06: 38; 2001-07-13: 29; 2001-07-20: 34; 2001-07-27: 40; 2001-08-03: 39; 2001-08-10: 40; 2001-08-17: 40; 2001-08-24: 40; 2001-08-31: 37; 2001-09-07: 35; 2001-09-14: 29; 2001-09-21: 31; 2001-09-28: 30; 2001-10-05: 29; 2001-10-12: 29; 2001-10-19: 26; 2001-10-26: 25; 2001-11-02: 16; 2001-11-09: 20; 2001-11-16: 14; 2001-11-23: 16 | 25
Bromodichloromethane | µg/L |  |  | 2001-06-08: 12; 2001-06-15: 10; 2001-06-22: 13; 2001-06-29: 13; 2001-07-06: 17; 2001-07-13: 13; 2001-07-20: 14; 2001-07-27: 15; 2001-08-03: 14; 2001-08-10: 14; 2001-08-17: 14; 2001-08-24: 13; 2001-08-31: 13; 2001-09-07: 11; 2001-09-14: 9; 2001-09-21: 10; 2001-09-28: 10; 2001-10-05: 9; 2001-10-12: 10; 2001-10-19: 9; 2001-10-26: 9; 2001-11-02: 6; 2001-11-09: 8; 2001-11-16: 5; 2001-11-23: 6 | 25
Chlorodibromomethane | µg/L |  |  | 2001-06-08: 3; 2001-06-15: 2; 2001-06-22: 3; 2001-06-29: 3; 2001-07-06: 4; 2001-07-13: 3; 2001-07-20: 3; 2001-07-27: 3; 2001-08-03: 3; 2001-08-10: 2; 2001-08-17: 0; 2001-08-24: 2; 2001-08-31: 2; 2001-09-07: 2; 2001-09-14: 2; 2001-09-21: 2; 2001-09-28: 2; 2001-10-05: 1; 2001-10-12: 2; 2001-10-19: 2; 2001-10-26: 2; 2001-11-02: 1; 2001-11-09: 2; 2001-11-16: 1; 2001-11-23: 1 | 25
Bromoform | µg/L |  |  | 2001-06-08: 0; 2001-06-15: 0; 2001-06-22: 0; 2001-06-29: 1; 2001-07-06: 0; 2001-07-13: 0; 2001-07-20: 0; 2001-07-27: 0; 2001-08-03: 0; 2001-08-10: 0; 2001-08-17: 0; 2001-08-24: 0; 2001-08-31: 0; 2001-09-07: 0; 2001-09-14: 0; 2001-09-21: 0; 2001-09-28: 0; 2001-10-05: 0; 2001-10-12: 0; 2001-10-19: 0; 2001-10-26: 0; 2001-11-02: 0; 2001-11-09: 0; 2001-11-16: 0; 2001-11-23: 0 | 25
BIOLOGICAL |  | CY Chart
Blue Green Algae | per litre |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 200 |  | 1200 | 0 | 0 | 0 | 0 | 400 | 0 | 400 | 0 | 800 | 200 | 400 | 200 | 2600 | 6000 | 10600 | 5800 |  | 3400 | 1400 | 14200 | 14400 | 41800 | 3400 | 3200 | 10200 | 25000 | 17800 | 8200 | 1800 | 5400 | 3000 | 4800 | 4400 | 3600 | 220 | 800 | 800 | 2000 | 600 | 800 | 600
Green Algae | per litre |  |  |  | 14400 | 7800 | 17000 | 9800 | 15800 | 28200 | 25200 |  | 54800 | 27400 | 14800 | 53600 | 24400 | 26600 | 34000 | 112800 | 200 | 0 | 0 | 200 | 400 | 1400 | 1000 | 600 | 2800 |  | 3000 | 400 | 1400 | 25600 | 29600 | 4600 | 3600 | 0 | 800 | 0 | 800 | 200 | 200 | 1000 | 0 | 0 | 400 | 200 | 200 | 0 | 1800 | 1600 | 800 | 2200
Diatoms | per litre |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 200 | 0 | 0 | 200 | 0 | 600 | 0 | 600 |  | 1400 | 400 | 200 | 1200 | 800 | 0 | 400 | 0 | 400 | 200 | 600 | 400 | 600 | 400 | 200 | 600 | 0 | 0 | 0 | 0 | 200 | 200 | 400 | 200
Flagellates | per litre |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 400
Crustaceans | per litre |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nematodes | per litre |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rotifers | per litre |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 200 | 200 | 400 | 200 | 0 | 0 | 400 | 0 | 400 | 200 | 0 | 0 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0
Other | per litre |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BACTERIOLOGICAL
Total Coliforms | per 100 ml |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Faecal Coliforms | per 100 ml
Faecal Streptococci | per 100 ml |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Standard Plate Count | per 1 mL |  |  | 0 | 0 | 0 | 0 | 0.04 | 0 | 0 | 0 |  | 0 | 0 | 0.02 | 0.1 | 0 | 0 | 0.03 | 0.02 | 0.04 | 0.06 | 0 | 0 | 0 | 0.04 | 0.12 | 0.2 | 0.1 | 0.2 | 0.4 | 0.3 | 8.9 | 35 | 16 | 8.4 | 9.4 | 6.6 | 4.2 | 4 | 2.7 | 3.6 | 2.1 | 1.6 | 0.7 | 1 | 0.8 | 0.6 | 0.3 | 0.1 | 0.02 | 0.02 | 0.1 | 0 | 0
RAW WATER ION BALANCE (SILICA NOT ADDED TO POSITIVE ION SUM)
Positive Ion sum | (meq/L) |  |  | #VALUE! | 7.7326 | 7.7659 | 7.6863 | 7.8142 | 7.8619 | #VALUE! | 7.9258 | #VALUE! | 8.0461 | 8.1718 | 8.0077 | 7.8769 | 7.8756 | 7.7221 | 7.7931 | 8.1769 | 6.0825 | 5.8966 | 6.435 | 6.3307 | 6.4078 | 6.4689 | 6.5498 | 6.4027 | 6.1708 | uncalcuable | 6.1247 | 5.9753 | 5.6686 | 5.9241 | 5.6088 | 5.548 | 5.6062 | 5.5976 | 5.6471 | 5.5601 | 5.5141 | 5.5566 | 5.6462 | 5.6177 | 5.7434 | 5.761 | 5.7447 | 5.8381 | 5.7623 | 5.7946 | 5.8122 | 6.2008 | 6.3118 | 6.5197 | #VALUE! | 47
Negative Ion Sum | (meq/L) |  |  | #VALUE! | 7.5813 | 7.5785 | 7.6069 | 7.7105 | 7.7013 | #VALUE! | 7.8234 | #VALUE! | 8.009 | 8.0282 | 7.9482 | 7.9202 | 7.6681 | 7.6192 | 7.5901 | 7.9442 | 5.9506 | 6.0374 | 6.1463 | 6.25 | 6.3748 | 6.4205 | 6.4867 | 6.3198 | 6.1087 | #VALUE! | 6.0525 | 6.0285 | 5.5009 | 5.6266 | 5.431 | 5.4108 | 5.4348 | 5.526 | 5.5005 | 5.5359 | 5.4468 | 5.5131 | 5.5646 | 5.4928 | 5.722 | 5.7102 | 5.6451 | 5.7338 | 5.6866 | 5.8022 | 5.795 | 6.0651 | 6.2344 | 6.3636 | #VALUE! | 47
Difference |  | CY Chart |  | #VALUE! | 0.15136 | 0.18744 | 0.0794 | 0.1037 | 0.16054 | #VALUE! | 0.10248 | #VALUE! | 0.03708 | 0.14356 | 0.05952 | 0.04328 | 0.20756 | 0.10284 | 0.20296 | 0.23274 | 0.13184 | 0.14078 | 0.28862 | 0.0807 | 0.03294 | 0.04838 | 0.06308 | 0.08284 | 0.0621 | #VALUE! | 0.07222 | 0.05316 | 0.16764 | 0.29754 | 0.17772 | 0.13724 | 0.17138 | 0.07152 | 0.14668 | 0.02424 | 0.06726 | 0.04356 | 0.08156 | 0.12496 | 0.02142 | 0.0508 | 0.09962 | 0.1043 | 0.07574 | 0.00762 | 0.0172 | 0.13572 | 0.07746 | 0.15612 | #VALUE! | 47
% Error |  |  |  | #VALUE! | 1.9768 | 2.4431 | 1.0384 | 1.3359 | 2.0631 | #VALUE! | 1.3014 | #VALUE! | 0.46191 | 1.7723 | 0.74606 | 0.54795 | 2.6707 | 1.3407 | 2.6387 | 2.8874 | 2.1913 | 2.3593 | 4.5881 | 1.2829 | 0.51539 | 0.7507 | 0.96774 | 1.3023 | 1.0114 | #VALUE! | 1.1862 | 0.88572 | 3.0017 | 5.1519 | 3.2196 | 2.5047 | 3.1044 | 1.2859 | 2.6316 | 0.43691 | 1.2273 | 0.78701 | 1.455 | 2.2494 | 0.37365 | 0.88569 | 1.7493 | 1.8026 | 1.3231 | 0.13142 | 0.29637 | 2.213 | 1.2348 | 2.4236 | #VALUE! | 47
Acceptable Difference | (meq/L) |  |  | #VALUE! | 0.22401 | 0.22397 | 0.22441 | 0.22601 | 0.22587 | #VALUE! | 0.22776 | #VALUE! | 0.23064 | 0.23094 | 0.2297 | 0.22926 | 0.22535 | 0.2246 | 0.22415 | 0.22963 | 0.19873 | 0.20008 | 0.20177 | 0.20338 | 0.20531 | 0.20602 | 0.20704 | 0.20446 | 0.20118 | #VALUE! | 0.20031 | 0.19994 | 0.19176 | 0.19371 | 0.19068 | 0.19037 | 0.19074 | 0.19215 | 0.19176 | 0.19231 | 0.19093 | 0.19195 | 0.19275 | 0.19164 | 0.19519 | 0.19501 | 0.194 | 0.19537 | 0.19464 | 0.19643 | 0.19632 | 0.20051 | 0.20313 | 0.20514 | #VALUE! | 47
(0.1065+(0.0155*neg ion sum))
Normal Ion Balance in % |  |  |  | #VALUE! | 0.98838 | 1.2216 | 0.51919 | 0.66797 | 1.0315 | #VALUE! | 0.6507 | #VALUE! | 0.23095 | 0.88617 | 0.37303 | -0.27397 | 1.3353 | 0.67035 | 1.3194 | 1.4437 | 1.0956 | -1.1796 | 2.294 | 0.64146 | 0.25769 | 0.37535 | 0.48387 | 0.65113 | 0.50572 | #VALUE! | 0.59308 | -0.44286 | 1.5009 | 2.5759 | 1.6098 | 1.2523 | 1.5522 | 0.64296 | 1.3158 | 0.21846 | 0.61364 | 0.39351 | 0.72751 | 1.1247 | 0.18682 | 0.44285 | 0.87464 | 0.90132 | 0.66155 | -0.065708 | 0.14818 | 1.1065 | 0.6174 | 1.2118 | #VALUE! | 47
(Standard Methods)
TREATED WATER ION BALANCE (SILICA NOT ADDED TO POSITIVE ION SUM)
Positive Ion sum | (meq/L) |  |  | #VALUE! | 7.6005 | 7.7186 | 7.7659 | 7.8388 | 7.8568 | #VALUE! | 7.8734 | #VALUE! | 8.0784 | 8.1193 | 7.9578 | 7.9204 | 7.8257 | 7.6696 | 7.8107 | 8.1334 | 6.2718 | 5.9453 | 6.2731 | 6.4129 | 6.4078 | 6.5536 | 6.5063 | 6.3729 | 6.1733 | uncalcuable | 6.1273 | 6.0546 | 5.7357 | 5.6897 | 5.6436 | 5.5941 | 5.6385 | 5.5976 | 5.6794 | 5.5924 | 5.5489 | 5.5553 | 5.6436 | 5.6526 | 5.7434 | 5.7434 | 5.6948 | 5.8381 | 5.7946 | 5.8381 | 5.8445 | 5.984 | 6.3441 | 6.5197 | #VALUE! | 47
Negative Ion Sum | (meq/L) |  |  | #VALUE! | 7.4922 | 7.6343 | 7.5863 | 7.7108 | 7.7079 | #VALUE! | 7.8388 | #VALUE! | 8.056 | 8.048 | 7.9303 | 7.9151 | 7.6265 | 7.5718 | 7.8086 | 7.9398 | 6.137 | 6.1557 | 6.2153 | 6.2001 | 6.3285 | 6.5094 | 6.441 | 6.3524 | 6.1512 | #VALUE! | 6.1124 | 5.9381 | 5.7162 | 5.8383 | 5.4839 | 5.4618 | 5.4888 | 5.4852 | 5.5452 | 5.5637 | 5.5075 | 5.5579 | 5.5826 | 5.5909 | 5.7515 | 5.7154 | 5.6971 | 5.7264 | 5.7063 | 5.7771 | 5.8351 | 6.122 | 6.2332 | 6.3773 | #VALUE! | 47
Difference |  |  |  | #VALUE! | 0.10838 | 0.0843 | 0.1796 | 0.12808 | 0.14882 | #VALUE! | 0.03462 | #VALUE! | 0.02242 | 0.0713 | 0.02754 | 0.00528 | 0.19926 | 0.09782 | 0.0021 | 0.19364 | 0.13482 | 0.21046 | 0.05782 | 0.21276 | 0.07926 | 0.04424 | 0.06532 | 0.0205 | 0.0221 | #VALUE! | 0.01482 | 0.11658 | 0.0195 | 0.14858 | 0.15974 | 0.13222 | 0.1497 | 0.11234 | 0.13426 | 0.02876 | 0.04144 | 0.0026 | 0.061 | 0.06164 | 0.00808 | 0.02802 | 0.0023 | 0.1117 | 0.08828 | 0.06102 | 0.00938 | 0.138 | 0.1109 | 0.14244 | #VALUE! | 47
% Error |  | CY Chart |  | #VALUE! | 1.4362 | 1.0982 | 2.3397 | 1.6474 | 1.9123 | #VALUE! | 0.44068 | #VALUE! | 0.27792 | 0.88202 | 0.34667 | 0.066686 | 2.5791 | 1.2836 | 0.02689 | 2.4095 | 2.173 | 3.4784 | 0.92598 | 3.3737 | 1.2446 | 0.67733 | 1.009 | 0.32219 | 0.35863 | #VALUE! | 0.24216 | 1.9442 | 0.34055 | 2.5777 | 2.8711 | 2.3918 | 2.6907 | 2.0273 | 2.3922 | 0.51559 | 0.74961 | 0.046791 | 1.0867 | 1.0965 | 0.14058 | 0.48906 | 0.04038 | 1.9318 | 1.5352 | 1.0507 | 0.16062 | 2.2799 | 1.7635 | 2.2089 | #VALUE! | 47
Acceptable Difference | (meq/L) |  |  | #VALUE! | 0.22263 | 0.22483 | 0.22409 | 0.22602 | 0.22597 | #VALUE! | 0.228 | #VALUE! | 0.23137 | 0.23124 | 0.22942 | 0.22918 | 0.22471 | 0.22386 | 0.22753 | 0.22957 | 0.20162 | 0.20191 | 0.20284 | 0.2026 | 0.20459 | 0.2074 | 0.20634 | 0.20496 | 0.20184 | #VALUE! | 0.20124 | 0.19854 | 0.1951 | 0.19699 | 0.1915 | 0.19116 | 0.19158 | 0.19152 | 0.19245 | 0.19274 | 0.19187 | 0.19265 | 0.19303 | 0.19316 | 0.19565 | 0.19509 | 0.19481 | 0.19526 | 0.19495 | 0.19604 | 0.19694 | 0.20139 | 0.20311 | 0.20535 | #VALUE! | 47
(0.1065+(0.0155*neg ion sum))
Normal Ion Balance in % |  |  |  | #VALUE! | 0.7181 | 0.54908 | 1.1699 | 0.82369 | 0.95614 | #VALUE! | 0.22034 | #VALUE! | 0.13896 | 0.44101 | 0.17334 | 0.033343 | 1.2895 | 0.6418 | 0.013445 | 1.2047 | 1.0865 | -1.7392 | 0.46299 | 1.6868 | 0.62232 | 0.33867 | 0.50451 | 0.1611 | 0.17932 | #VALUE! | 0.12108 | 0.97209 | 0.17028 | -1.2889 | 1.4355 | 1.1959 | 1.3453 | 1.0136 | 1.1961 | 0.2578 | 0.3748 | -0.023395 | 0.54337 | 0.54823 | -0.070292 | 0.24453 | -0.02019 | 0.96589 | 0.76759 | 0.52535 | 0.080311 | -1.1399 | 0.88174 | 1.1044 | #VALUE! | 47
(Standard Methods)
6478.2428
| Raw |  | A = | 2.5304 | 2.5328 | 2.5232 | 2.5184 | 2.5256 | 2.5208 | 2.5136 | 2.5208 | uncalcuable | 2.516 | 2.5064 | 2.5184 | 2.492 | 2.4824 | 2.468 | 2.4488 | 2.4296 | 2.408 | 2.3384 | 2.2592 | 2.3048 | 2.2208 | 2.2328 | 2.1896 | 2.1848 | 2.1128 | 2.1392 | 2.0984 | 2.0888 | 2.06 | 2.0816 | 2.0384 | 2.096 | 2.096 | 2.1176 | 2.1656 | 2.216 | 2.2376 | 2.276 | 2.2472 | 2.3624 | 2.4488 | 2.4608 | 2.5112 | 2.504 | 2.5256 | 2.5376 | 2.588 | 2.5688 | 2.5592 | 2.5448 | 2.5376
|  |  | log TDS = | #VALUE! | 2.753 | 2.754 | 2.7544 | 2.7613 | 2.7612 | #VALUE! | 2.7671 | #VALUE! | 2.7766 | 2.7791 | 2.7739 | 2.7713 | 2.7607 | 2.7566 | 2.7547 | 2.7762 | 2.6496 | 2.6529 | 2.6664 | 2.6701 | 2.6782 | 2.6821 | 2.6842 | 2.6701 | 2.6584 | #VALUE! | 2.6576 | 2.655 | 2.6114 | 2.6269 | 2.6098 | 2.6085 | 2.6139 | 2.6143 | 2.6149 | 2.6207 | 2.6122 | 2.6143 | 2.616 | 2.615 | 2.6306 | 2.6322 | 2.6301 | 2.6374 | 2.6345 | 2.6415 | 2.6411 | 2.6619 | 2.674 | 2.6833 | #VALUE!
|  |  | B = | #VALUE! | 9.8753 | 9.8754 | 9.8754 | 9.8761 | 9.8761 | #VALUE! | 9.8767 | #VALUE! | 9.8777 | 9.8779 | 9.8774 | 9.8771 | 9.8761 | 9.8757 | 9.8755 | 9.8776 | 9.865 | 9.8653 | 9.8666 | 9.867 | 9.8678 | 9.8682 | 9.8684 | 9.867 | 9.8658 | #VALUE! | 9.8658 | 9.8655 | 9.8611 | 9.8627 | 9.861 | 9.8608 | 9.8614 | 9.8614 | 9.8615 | 9.8621 | 9.8612 | 9.8614 | 9.8616 | 9.8615 | 9.8631 | 9.8632 | 9.863 | 9.8637 | 9.8634 | 9.8641 | 9.8641 | 9.8662 | 9.8674 | 9.8683 | #VALUE!
|  |  | Log(Ca) = | uncalcuable | 2.1833 | 2.1833 | 2.1833 | 2.1973 | 2.1903 | uncalcuable | 2.2041 | uncalcuable | 2.2175 | 2.2175 | 2.2175 | 2.2175 | 2.2109 | 2.1973 | 2.1903 | 2.2175 | 2.1055 | 2.0792 | 2.1139 | 2.1222 | 2.1222 | 2.1383 | 2.1303 | 2.1055 | 2.0792 | 2.1139 | 2.0792 | 2.0969 | 2.0414 | 2.0512 | 2.0314 | 2.0607 | 2.0314 | 2.0212 | 2.0314 | 2.0314 | 2.0314 | 2.0414 | 2.0414 | 2.0607 | 2.0607 | 2.0792 | 2.07 | 2.0792 | 2.0881 | 2.0792 | 2.0969 | 2.1055 | 2.1303 | 2.1303 | uncalcuable
|  |  | Log(alk)= | 2.3096 | 2.3054 | 2.3054 | 2.3096 | 2.3139 | 2.3096 | 2.3139 | 2.3201 | uncalcuable | 2.3324 | 2.3345 | 2.3304 | 2.3324 | 2.3181 | 2.3201 | 2.3118 | 2.3385 | 2.2122 | 2.2304 | 2.2253 | 2.2304 | 2.243 | 2.2455 | 2.2455 | 2.2253 | 2.2041 | 2.1903 | 2.1987 | 2.2068 | 2.1399 | 2.1584 | 2.1461 | 2.1644 | 2.1584 | 2.1644 | 2.1584 | 2.1614 | 2.1614 | 2.1761 | 2.179 | 2.1875 | 2.1959 | 2.1959 | 2.1959 | 2.2041 | 2.2041 | 2.2122 | 2.2148 | 2.233 | 2.2455 | 2.2553 | uncalcuable
| CW |  | A = | 2.5304 | 2.5328 | 2.5232 | 2.5184 | 2.5256 | 2.5208 | 2.5136 | 2.5208 | uncalcuable | 2.516 | 2.5064 | 2.5184 | 2.492 | 2.4824 | 2.468 | 2.4488 | 2.4296 | 2.408 | 2.3384 | 2.2592 | 2.3048 | 2.2208 | 2.2328 | 2.1896 | 2.1848 | 2.1128 | 2.1392 | 2.0984 | 2.0888 | 2.06 | 2.0816 | 2.0384 | 2.096 | 2.096 | 2.1176 | 2.1656 | 2.216 | 2.2376 | 2.276 | 2.2472 | 2.3624 | 2.4488 | 2.4608 | 2.5112 | 2.504 | 2.5256 | 2.5376 | 2.588 | 2.5688 | 2.5592 | 2.5448 | 2.5376
|  |  | log TDS = | #VALUE! | 2.7409 | 2.7484 | 2.7468 | 2.7534 | 2.754 | #VALUE! | 2.7591 | #VALUE! | 2.771 | 2.7713 | 2.7651 | 2.7643 | 2.7493 | 2.7438 | 2.755 | 2.7664 | 2.6522 | 2.648 | 2.657 | 2.658 | 2.6657 | 2.6778 | 2.6734 | 2.6656 | 2.6511 | #VALUE! | 2.6486 | 2.6368 | 2.6177 | uncalcuable | 2.6036 | 2.604 | 2.6042 | 2.6014 | 2.6079 | 2.6066 | 2.6053 | 2.6072 | 2.6107 | 2.613 | 2.6217 | 2.6211 | 2.6198 | 2.6261 | 2.624 | 2.6308 | 2.6344 | 2.6531 | 2.6647 | 2.6755 | #VALUE!
|  |  | B = | #VALUE! | 9.8741 | 9.8748 | 9.8747 | 9.8753 | 9.8754 | #VALUE! | 9.8759 | #VALUE! | 9.8771 | 9.8771 | 9.8765 | 9.8764 | 9.8749 | 9.8744 | 9.8755 | 9.8766 | 9.8652 | 9.8648 | 9.8657 | 9.8658 | 9.8666 | 9.8678 | 9.8673 | 9.8666 | 9.8651 | #VALUE! | 9.8649 | 9.8637 | 9.8618 | #VALUE! | 9.8604 | 9.8604 | 9.8604 | 9.8601 | 9.8608 | 9.8607 | 9.8605 | 9.8607 | 9.8611 | 9.8613 | 9.8622 | 9.8621 | 9.862 | 9.8626 | 9.8624 | 9.8631 | 9.8634 | 9.8653 | 9.8665 | 9.8676 | #VALUE!
|  |  | Log(Ca) = | uncalcuable | 2.1761 | 2.1761 | 2.1833 | 2.1903 | 2.1903 | uncalcuable | 2.1973 | uncalcuable | 2.2109 | 2.2109 | 2.2109 | 2.2175 | 2.2041 | 2.1903 | 2.2041 | 2.2175 | 2.1222 | 2.0792 | 2.1139 | 2.1222 | 2.1222 | 2.1383 | 2.1303 | 2.1139 | 2.0792 | 2.0792 | 2.0792 | 2.0512 | 2.0212 | 2.0212 | 2.0212 | 2.0607 | 2.0212 | 2.0212 | 2.0212 | 2.0212 | 2.0212 | 2.0314 | 2.0414 | 2.0512 | 2.0607 | 2.0607 | 2.0607 | 2.0792 | 2.0792 | 2.0792 | 2.0881 | 2.0969 | 2.1222 | 2.1303 | uncalcuable
|  |  | Log(alk)= | 2.2201 | 2.2279 | 2.2355 | 2.233 | 2.2355 | 2.2355 | 2.2405 | 2.2455 | uncalcuable | 2.2601 | 2.2577 | 2.2553 | 2.2553 | 2.2227 | 2.2201 | 2.233 | 2.2504 | 2.1139 | 2.1173 | 2.1173 | 2.1173 | 2.1399 | 2.1492 | 2.1399 | 2.1139 | 2.0828 | 2.0719 | 2.0828 | 2.0607 | 2.0294 | 2.0492 | 2.0086 | 2.0043 | 2 | 1.9731 | 1.9868 | 1.9823 | 2.0086 | 2.0212 | 2.0212 | 2.0374 | 2.0294 | 2.0453 | 2.0569 | 2.0755 | 2.0828 | 2.1139 | 2.1303 | 2.1492 | 2.1614 | 2.179 | uncalcuable
RAW WATER ION BALANCE 1996 (SILICA ADDED TO POSITIVE ION SUM)
Positive Ion sum | (meq/L) |  |  | #VALUE! | 7.9272 | 7.9841 | 7.8895 | 8.0335 | 8.0864 | #VALUE! | 8.1569 | #VALUE! | 8.288 | 8.4229 | 8.2546 | 8.118 | 8.0954 | 7.945 | 8.0165 | 8.4072 | 6.2344 | 6.0596 | 6.6069 | 6.4848 | 6.5823 | 6.6424 | 6.7265 | 6.5904 | 6.3821 | 4.2984 | 6.3663 | 6.2119 | 5.9102 | 6.1781 | 5.8822 | 5.828 | 5.9085 | 5.9041 | 5.9716 | 5.8656 | 5.8056 | 5.8569 | 5.9511 | 5.9356 | 6.0458 | 6.0615 | 6.0292 | 6.0986 | 6.0305 | 6.0812 | 6.0659 | 6.4753 | 6.6015 | 6.8121 | #VALUE!
Negative Ion Sum | (meq/L) |  |  | #VALUE! | 7.5813 | 7.5785 | 7.6069 | 7.7105 | 7.7013 | #VALUE! | 7.8234 | #VALUE! | 8.009 | 8.0282 | 7.9482 | 7.9202 | 7.6681 | 7.6192 | 7.5901 | 7.9442 | 5.9506 | 6.0374 | 6.1463 | 6.25 | 6.3748 | 6.4205 | 6.4867 | 6.3198 | 6.1087 | #VALUE! | 6.0525 | 6.0285 | 5.5009 | 5.6266 | 5.431 | 5.4108 | 5.4348 | 5.526 | 5.5005 | 5.5359 | 5.4468 | 5.5131 | 5.5646 | 5.4928 | 5.722 | 5.7102 | 5.6451 | 5.7338 | 5.6866 | 5.8022 | 5.795 | 6.0651 | 6.2344 | 6.3636 | #VALUE!
Difference |  |  |  | #VALUE! | 0.34591 | 0.40565 | 0.28262 | 0.32296 | 0.38506 | #VALUE! | 0.33357 | #VALUE! | 0.27895 | 0.39463 | 0.30638 | 0.1978 | 0.42734 | 0.32578 | 0.42642 | 0.46304 | 0.2838 | 0.022218 | 0.46056 | 0.23476 | 0.20751 | 0.22189 | 0.23975 | 0.27055 | 0.27347 | #VALUE! | 0.31383 | 0.18345 | 0.40925 | 0.5515 | 0.45114 | 0.41723 | 0.47371 | 0.37806 | 0.4711 | 0.32973 | 0.35882 | 0.34379 | 0.38652 | 0.44281 | 0.32375 | 0.35129 | 0.38408 | 0.36483 | 0.3439 | 0.27894 | 0.2709 | 0.41019 | 0.36718 | 0.44846 | #VALUE!
YTD Average
% Error |  | CY Chart |  | #VALUE! | 4.4609 | 5.2131 | 3.6476 | 4.1026 | 4.8779 | #VALUE! | 4.1748 | #VALUE! | 3.4233 | 4.7976 | 3.7819 | 2.4666 | 5.422 | 4.1862 | 5.4647 | 5.6636 | 4.6581 | 0.36733 | 7.2226 | 3.6869 | 3.2029 | 3.3973 | 3.6289 | 4.1913 | 4.3788 | #VALUE! | 5.054 | 2.9974 | 7.1727 | 9.3438 | 7.9754 | 7.4248 | 8.3523 | 6.6152 | 8.213 | 5.784 | 6.3776 | 6.0474 | 6.713 | 7.7493 | 5.5024 | 5.9684 | 6.5799 | 6.1667 | 5.8701 | 4.6946 | 4.5679 | 6.5419 | 5.7211 | 6.8075 | #VALUE! | #VALUE!
Acceptable Difference | (meq/L) |  |  | #VALUE! | 0.22401 | 0.22397 | 0.22441 | 0.22601 | 0.22587 | #VALUE! | 0.22776 | #VALUE! | 0.23064 | 0.23094 | 0.2297 | 0.22926 | 0.22535 | 0.2246 | 0.22415 | 0.22963 | 0.19873 | 0.20008 | 0.20177 | 0.20338 | 0.20531 | 0.20602 | 0.20704 | 0.20446 | 0.20118 | #VALUE! | 0.20031 | 0.19994 | 0.19176 | 0.19371 | 0.19068 | 0.19037 | 0.19074 | 0.19215 | 0.19176 | 0.19231 | 0.19093 | 0.19195 | 0.19275 | 0.19164 | 0.19519 | 0.19501 | 0.194 | 0.19537 | 0.19464 | 0.19643 | 0.19632 | 0.20051 | 0.20313 | 0.20514 | #VALUE!
(0.1065+(0.0155*neg ion sum))
Normal Ion Balance in % |  |  |  | #VALUE! | 2.2304 | 2.6066 | 1.8238 | 2.0513 | 2.439 | #VALUE! | 2.0874 | #VALUE! | 1.7117 | 2.3988 | 1.8909 | 1.2333 | 2.711 | 2.0931 | 2.7323 | 2.8318 | 2.329 | 0.18366 | 3.6113 | 1.8435 | 1.6015 | 1.6987 | 1.8145 | 2.0956 | 2.1894 | #VALUE! | 2.527 | 1.4987 | 3.5864 | 4.6719 | 3.9877 | 3.7124 | 4.1761 | 3.3076 | 4.1065 | 2.892 | 3.1888 | 3.0237 | 3.3565 | 3.8746 | 2.7512 | 2.9842 | 3.29 | 3.0833 | 2.935 | 2.3473 | 2.284 | 3.2709 | 2.8605 | 3.4037 | #VALUE!
(Standard Methods)
TREATED WATER ION BALANCE 1996 (SILICA ADDED TO POSITIVE ION SUM)
Positive Ion sum | (meq/L) |  |  | #VALUE! | 7.7964 | 7.927 | 7.9699 | 8.0518 | 8.0726 | #VALUE! | 8.0884 | #VALUE! | 8.3111 | 8.3557 | 8.1997 | 8.1586 | 8.0481 | 7.8841 | 8.0131 | 8.3543 | 6.4159 | 6.087 | 6.4227 | 6.553 | 6.5584 | 6.7198 | 6.6761 | 6.5491 | 6.3715 | 4.3259 | 6.335 | 6.2681 | 5.9621 | 5.9234 | 5.8897 | 5.8556 | 5.914 | 5.8783 | 5.9723 | 5.8919 | 5.8668 | 5.8364 | 5.9265 | 5.946 | 6.0287 | 6.025 | 5.9619 | 6.122 | 6.0596 | 6.1013 | 6.0908 | 6.2471 | 6.601 | 6.786 | #VALUE!
Negative Ion Sum | (meq/L) |  |  | #VALUE! | 7.4922 | 7.6343 | 7.5863 | 7.7108 | 7.7079 | #VALUE! | 7.8388 | #VALUE! | 8.056 | 8.048 | 7.9303 | 7.9151 | 7.6265 | 7.5718 | 7.8086 | 7.9398 | 6.137 | 6.1557 | 6.2153 | 6.2001 | 6.3285 | 6.5094 | 6.441 | 6.3524 | 6.1512 | #VALUE! | 6.1124 | 5.9381 | 5.7162 | 5.8383 | 5.4839 | 5.4618 | 5.4888 | 5.4852 | 5.5452 | 5.5637 | 5.5075 | 5.5579 | 5.5826 | 5.5909 | 5.7515 | 5.7154 | 5.6971 | 5.7264 | 5.7063 | 5.7771 | 5.8351 | 6.122 | 6.2332 | 6.3773 | #VALUE!
Difference |  |  |  | #VALUE! | 0.30424 | 0.29278 | 0.38361 | 0.34103 | 0.36466 | #VALUE! | 0.24967 | #VALUE! | 0.25509 | 0.30765 | 0.26941 | 0.24347 | 0.42167 | 0.31235 | 0.20453 | 0.41448 | 0.27889 | 0.068757 | 0.20741 | 0.35289 | 0.2299 | 0.21039 | 0.23515 | 0.19664 | 0.22033 | #VALUE! | 0.22251 | 0.33005 | 0.24586 | 0.085138 | 0.40581 | 0.39381 | 0.42522 | 0.39312 | 0.42713 | 0.3282 | 0.35929 | 0.27844 | 0.34388 | 0.35504 | 0.27717 | 0.30959 | 0.26481 | 0.39563 | 0.35328 | 0.32418 | 0.25572 | 0.12516 | 0.36775 | 0.40876 | #VALUE!
YTD Average
% Error |  | CY Chart |  | #VALUE! | 3.98 | 3.7629 | 4.9319 | 4.3271 | 4.6217 | #VALUE! | 3.1352 | #VALUE! | 3.1171 | 3.7509 | 3.3405 | 3.0294 | 5.3803 | 4.0418 | 2.5855 | 5.0875 | 4.4434 | 1.1232 | 3.2823 | 5.5341 | 3.568 | 3.1807 | 3.5854 | 3.0484 | 3.5188 | #VALUE! | 3.5752 | 5.408 | 4.2105 | 1.4477 | 7.1361 | 6.9592 | 7.4581 | 6.9189 | 7.4171 | 5.73 | 6.3175 | 4.8873 | 5.9758 | 6.1548 | 4.7056 | 5.2739 | 4.5425 | 6.6782 | 6.0052 | 5.4584 | 4.2884 | 2.0238 | 5.7308 | 6.2106 | #VALUE! | #VALUE!
Acceptable Difference | (meq/L) |  |  | #VALUE! | 0.22263 | 0.22483 | 0.22409 | 0.22602 | 0.22597 | #VALUE! | 0.228 | #VALUE! | 0.23137 | 0.23124 | 0.22942 | 0.22918 | 0.22471 | 0.22386 | 0.22753 | 0.22957 | 0.20162 | 0.20191 | 0.20284 | 0.2026 | 0.20459 | 0.2074 | 0.20634 | 0.20496 | 0.20184 | #VALUE! | 0.20124 | 0.19854 | 0.1951 | 0.19699 | 0.1915 | 0.19116 | 0.19158 | 0.19152 | 0.19245 | 0.19274 | 0.19187 | 0.19265 | 0.19303 | 0.19316 | 0.19565 | 0.19509 | 0.19481 | 0.19526 | 0.19495 | 0.19604 | 0.19694 | 0.20139 | 0.20311 | 0.20535 | #VALUE!
(0.1065+(0.0155*neg ion sum))
Normal Ion Balance in % |  |  |  | #VALUE! | 1.99 | 1.8815 | 2.466 | 2.1635 | 2.3108 | #VALUE! | 1.5676 | #VALUE! | 1.5585 | 1.8755 | 1.6702 | 1.5147 | 2.6902 | 2.0209 | 1.2927 | 2.5437 | 2.2217 | -0.56162 | 1.6412 | 2.767 | 1.784 | 1.5904 | 1.7927 | 1.5242 | 1.7594 | #VALUE! | 1.7876 | 2.704 | 2.1052 | 0.72386 | 3.568 | 3.4796 | 3.7291 | 3.4595 | 3.7085 | 2.865 | 3.1588 | 2.4437 | 2.9879 | 3.0774 | 2.3528 | 2.6369 | 2.2713 | 3.3391 | 3.0026 | 2.7292 | 2.1442 | 1.0119 | 2.8654 | 3.1053 | #VALUE!
(Standard Methods)
CLEARWELL parameters for RTW | [55 empty] | CORRELATIONS |  | On Chart ?
Measured TDS | mg/L |  |  | uncalcuable | 550.65 | 560.33 | 558.26 | 566.8 | 567.51 | uncalcuable | 574.28 | #VALUE! | 590.25 | 590.59 | 582.3 | 581.16 | 561.46 | 554.36 | 568.9 | 584 | 448.98 | 444.59 | 453.89 | 455.03 | 463.13 | 476.22 | 471.36 | 463 | 447.84 | uncalcuable | 445.2 | 433.32 | 414.71 | 0 | 401.46 | 401.75 | 401.98 | 399.38 | 405.44 | 404.19 | 402.99 | 404.79 | 408.06 | 410.16 | 418.55 | 417.91 | 416.66 | 422.8 | 420.68 | 427.41 | 430.97 | 449.91 | 462.07 | 473.73 | #VALUE!
Measured temperature | deg C |  |  | 2.9 | 2.8 | 3.2 | 3.4 | 3.1 | 3.3 | 3.6 | 3.3 | 0 | 3.5 | 3.9 | 3.4 | 4.5 | 4.9 | 5.5 | 6.3 | 7.1 | 8 | 10.9 | 14.2 | 12.3 | 15.8 | 15.3 | 17.1 | 17.3 | 20.3 | 19.2 | 20.9 | 21.3 | 22.5 | 21.6 | 23.4 | 21 | 21 | 20.1 | 18.1 | 16 | 15.1 | 13.5 | 14.7 | 9.9 | 6.3 | 5.8 | 3.7 | 4 | 3.1 | 2.6 | 0.5 | 13 | 1.7 | 2.3 | 2.6 | CW Al (p) to alum/raw DOC: | -0.54212
Measured pH |  |  |  | 7.27 | 7.46 | 7.43 | 7.38 | 7.25 | 7.24 | 7.42 | 7.24 | 0 | 7.4 | 7.1 | 7.26 | 7.28 | 7.2 | 7.41 | 7.46 | 7.43 | 7.25 | 7.32 | 7.32 | 7.3 | 7.27 | 7.58 | 7.34 | 7.41 | 7.45 | 7.64 | 7.36 | 7.39 | 7.39 | 7.44 | 7.33 | 7.26 | 7.19 | 7.08 | 7.14 | 7.25 | 7.19 | 7.25 | 7.19 | 7.26 | 7.3 | 7.31 | 7.18 | 7.2 | 7.08 | 7.33 | 7.43 | 7.14 | 7.33 | 7.3 | 7.3 | PreCl2 to Chan THM's | 0.44563
Measured alk, as CaCO3 | mg/L |  |  | 166 | 169 | 172 | 171 | 172 | 172 | 174 | 176 | 0 | 182 | 181 | 180 | 180 | 167 | 166 | 171 | 178 | 130 | 131 | 131 | 131 | 138 | 141 | 138 | 130 | 121 | 118 | 121 | 115 | 107 | 112 | 102 | 101 | 100 | 94 | 97 | 96 | 102 | 105 | 105 | 109 | 107 | 111 | 114 | 119 | 121 | 130 | 135 | 141 | 145 | 151 | 0 | Total Cl2 to Raw DOC | 0.33978
Measured Ca, as CaCO3 | mg/L |  |  | 0 | 150 | 150 | 152.5 | 155 | 155 | 0 | 157.5 | 0 | 162.5 | 162.5 | 162.5 | 165 | 160 | 155 | 160 | 165 | 132.5 | 120 | 130 | 132.5 | 132.5 | 137.5 | 135 | 130 | 120 | 120 | 120 | 112.5 | 105 | 105 | 105 | 115 | 105 | 105 | 105 | 105 | 105 | 107.5 | 110 | 112.5 | 115 | 115 | 115 | 120 | 120 | 120 | 122.5 | 125 | 132.5 | 135 | 0 | Alum Dose to DOC removal: | 0.49329
Measured Cl | mg/L |  |  | 0 | 16.8 | 17.3 | 17.5 | 17.8 | 17.7 | 0 | 17.8 | 0 | 17.9 | 18.2 | 17.4 | 17.6 | 18.3 | 19 | 18.9 | 18.9 | 15.1 | 14.6 | 14.5 | 14.7 | 14.6 | 15 | 14.9 | 16.1 | 16.1 | 0 | 16.2 | 16.3 | 17.2 | 17.3 | 15.4 | 15.2 | 16 | 16.1 | 15.9 | 16.4 | 15.5 | 15.7 | 15.1 | 14.7 | 15.5 | 15 | 13.5 | 14 | 13.6 | 13.4 | 13.6 | 13.8 | 14.1 | 14.4 | 0 | Chlor A to T Grn & BG Algae | 0.60515
Measured SO4 | mg/L |  |  | 0 | 175 | 178 | 177 | 181 | 181 | 0 | 184 | 0 | 188 | 188 | 185 | 184 | 181 | 179 | 185 | 185 | 150 | 150 | 153 | 152 | 152 | 157 | 157 | 159 | 158 | 0 | 156 | 153 | 149 | 150 | 145 | 145 | 146 | 152 | 152 | 153 | 146 | 145 | 147 | 144 | 153 | 148 | 146 | 142 | 140 | 135 | 132 | 140 | 141 | 142 | 0
Note on E8: This is the only cell that needs a new date entered when making up a template for the next years data. All other date cells have formulas.
Note on S11: blair kardash 04/20/00 11:13:47 AM raw was collected from sp1. It was most likely contaminated with chlorine. The intake for the old wet well was from the new side as the fish screen was removed from the old side. chloride was the same for raw and cw
Note on A17: blair kardash 01/18/00 02:59:30 PM 1. If temperature or bench dissolved oxygen is not entered the calculation will return "uncalcuable". 2. The dissolved oxygen concentration in mg/L is divided by the saturation concentration of oxygen at the water temperature the sample was collected at. This value is multiplyed by 100 to express as a percentage. (The saturation of DO is determined using @vlookup for the table called TABLE OXYGEN.) 3. The table values are from Appendix 1 in the Orion Model 820 Instruction Manual.
Note on W33: Student using beaker to measure sample volume, not grad cylinder.
Note on A62: blair kardash 01/19/00 01:09:08 PM 1. The source of the NOM in water supplies greatly infuences the composition of the organic matter. Organic matter derived from algal and cyanobacterial biomass is mostly aliphatic and totally devoid of lignins thus does not strongly absorb at 254nm. NOM of soil origin tends to have a higher aromatic fraction than NOM of aquatic origin thus absorbs more strongly at 254nm. (lignin, tannin, humic substances and various aromatic compounds strongly absorb UV) 2. Strong correlations may exist between UV absorption and organic content, colour, and precursors to THM's. It can also be used to monitor organic removal by coagulation and carbon adsorption at BP. 3. see AWWA Journal - January 1995 "Biodegradation of NOM: effect of NOM source and ozone dose". pp 90-105. see Standard Methods 20th Edition: 5910 UV-Absorbing Constituents. pp 5-65 to 5-68.
Note on A63: blair kardash 01/19/00 12:06:06 PM 1. The ratio can provide an indication of the degree of unsaturation of the NOM in the source water thus can be used to characterize NOM. UV light is preferentially absorbed by unsaturated chemical bonds (without C-H bonds). 2. A higher UV-to-DOC ratio may suggest a larger fraction of organics may be from soil based humic substances. A higher UV-to-DOC ratio suggests that the NOM has a larger fraction of unsaturated organic compounds. Organic matter of terrestrial (land) origin is likely to have a higher degree of aromaticity because a substantial component of the organic matter consists of lignin. 3. Keeping track of this over time may aid in getting a handle on where additional organic materials contributing to an increasing level of DOC at BP Lake is derived from. 4. see AWWA Journal - January 1995 "Biodegradation of NOM: effect of NOM source and ozone dose". pp 90-105. see Standard Methods 20th Edition: 5910 UV-Absorbing Constituents. pp 5-65 to 5-68.
Note on A99: blair kardash 01/19/00 11:51:13 AM 1. The sum of Blue-Green and Green algae counts. 2. If either counts are not entered then the formula will return @ERR. 3. SIGNIFICANCE: These two algal types create the most problems with water treatment - odours, low and high DO, high Mn.
Note on F128: blair kardash 12/01/01 02:15:53 PM started to adjust pH to 4 using 850µL of 1N HCl. pH 4 buffer used previously was too weak to lower pH of CW to 4.
Note on W168: Student using beaker to measure sample volume, not grad cylinder.
Note on A207: blair kardash 06/06/00 11:07:01 AM 1. Clearwell DOC (or PreGAC DOC -if GAC's on) ÷ Raw DOC. 2. Indicator of sufficient alum dose.
Note on A208: blair kardash 06/06/00 11:54:21 AM 1. (PreGAC DOC - CW DOC) ÷ preGAC DOC. 2. Calculates the amount (after coagulation and filtration) of DOC removed by GAC's. 3. Indicates the efficiency of organic carbon removal by GAC. This decreases over time.
Note on A209: 1. (Raw DOC - CW DOC) ÷ Raw DOC 2. Measures the total amount of organic carbon removed by complete water treatment.

## Lagoons
Buffalo Pound WTP Lagoon Effluent : 1998-
Date Sample Collected | Lagoon | pH | Turbidity (NTU) | SST (mg/L) | SSV (mg/L) | SSF (mg/L) | DO (mg/L) | Colour (Pt/Co) | Free Chlorine (mg/L) | Combined Chlorine (mg/L) | Comments
1998-01-21 | Winter-SOUTH | 7.19 | 19.5 | 12 | 12 | 0 | 11.3 | 70
1998-01-30 | Winter-SOUTH | 7.34 | 22.9 | 56 | 23 | 33 | 11.1 | 80
1998-02-04 | Winter-SOUTH | 7.48 | 24.7 | 102 | 42 | 60 | 11.6 | 80
1998-02-12 | Winter-SOUTH | 7.29 | 2.59 | 5.6 | 2.8 | 2.8 | 10.7 | 20
1998-02-18 | Winter-SOUTH | 7.29 | 2.48 | 5.2 | 2.8 | 2.4 | 10.5 | 15
1998-02-27 | Winter-SOUTH | 7.47 | 120 | 1380 | 470 | 910 | 10.9 | 400
1998-03-06 | Winter-SOUTH | 7.27 | 50.4 | 410 | 190 | 220 | 11.1 | 250
1998-03-12 | Winter-SOUTH | 7.17 | 105 | 292 | 140 | 152 | 10.6 | 500
1998-03-13 | Winter-SOUTH |  | 604 | 1570
1998-03-19 | Summer-SW | 7.16 | 2.25 | 6.7 | 3 | 3.7 | 11.6 | 15 |  |  | switched lagoons
1998-03-26 | Summer-SW | 7.21 | 2.32 | 6 | 3.4 | 2.6 | 11.7 | 15
1998-04-03 | Summer-SW | 7.39 | 3.07 | 6.8 | 3.2 | 3.6 | 10.6 | 25
1998-04-16 | Summer-SW | 7.22 | 3.78 | 7.3 | 7 | 0.3 | 10.6 | 25
1998-04-24 | Summer-SW | 7.3 | 421 | 1360 | 585 | 775 | 9.2 | 1250 |  |  | extremely windy day
1998-04-28 | Summer-SW | 7.27 | 2.96 | 4.8 | 2.6 | 2.2 | 10.3 | 15
1998-05-05 | Summer-SW | 7.49 | 4.58 | 9.8 | 4.9 | 4.9 | 9.1 | 35
1998-05-15 | Summer-SW | 7.55 | 2.27 | 6.8 | 3.4 | 3.4 | 9 | 15
1998-05-29 | Summer-SW | 7.43 | 143 | 564 | 212 | 352 | 9.2 | 400
1998-06-09 | Summer-NE | 7.5 | 1.61 | 4.2 | 2.6 | 1.6 | 8 | 10 | 0 | 0 | switched lagoons
1998-06-16 | Summer-NE | 7.5 | 1.07 | 3.2 | 2.2 | 1 | 7.8 | 10 | 0 | 0
1998-06-26 | Summer-NE | 7.21 | 1.18 | 3.8 | 2.8 | 1 |  | 10 | 0 | 0
1998-07-09 | Summer-NE | 7.64 | 1.18 | 3.2 | 1.8 | 1.4 | 6.7 | 10
1998-07-17 | Summer-NE | 7.51 | 1.05 | 18 | 1.4 | 0.4 |  | 10 | < | <
1998-07-21 | Summer-NE | 7.45 | 3.61 | 8.8 | 5.2 | 3.6 | 6.6 | 15
1998-07-30 | Summer-NE | 7.32 | 4.06 | 9.2 | 7.2 | 2 | 6.6 | 20
1998-08-07 | Summer-NE | 7.49 | 6.32 | 19.6 | 10.8 | 8.8 | 7.6 | 25
1998-08-13 | Summer-NE | 7.22 | 109 | 392 | 172 | 220 | 7.5 | 300 |  |  | Gene notified of carryover
1998-08-18 | Summer-NW | 7.27 | 2.35 | 6.6 | 4.6 | 2 | 7.2 | 15 |  |  | switched lagoons
1998-08-24 | Summer-NW | 7.32 | 1.61 | 4.8 | 3.9 | 0.9 | 6.6 | 10
1998-09-03 | Summer-NW | 7.27 | 3.74 | 11 | 9.6 | 1.4 | 6.5 | 15
1998-09-17 | Summer-NW | 7.23 | 32.1 | 128 | 76 | 52 | 7.9 | 100
1998-09-29 | Summer-SE | 7.1 | 2.54 | 8.2 | 6.6 | 1.6 | 8.1 | 10 |  |  | Switched lagoons 24/9
1998-10-06 | Summer-SE | 7.58 | 2.99 | 6.6 | 4 | 2.6 | 8.1 | 10
1998-10-27 | Summer-SE | 7.46 | 3.67 | 9.3 | 5 | 4.3 | 10.9 | 10
1998-11-03 | Winter-East | 7.69 | 3.49 | 9.2 | 5.2 | 4 | 11.6 | 15 |  |  | Switched lagoons 30/10
1998-11-10 | Winter-East | 7.45 | 2.89 | 7.2 | 3.6 | 3.6 | 11 | 15
1998-11-17 | Winter-East | 7.49 | 2.94 | 7.6 | 4.4 | 3.2 | 12.7 | 15
1998-12-01 | Winter-East | 7.34 | 3.34 | 9.6 | 4.4 | 5.2 | 11.5 | 10
1998-12-11 | Winter-East | 7.53 | 2.31 |  |  |  |  | 5 |  |  | lab accident for tss
1998-12-15 | Winter-East | 7.36 | 2.19 | 5.5 | 2.5 | 3 | 12.2 | 10
1998-12-22 | Winter-East | 7.51 | 2.38 | 5.2 | 2.6 | 2.6 | 12 | 10
1999-01-05 | Winter-East | 7.21 | 2.46 | 5.2 | 2.6 | 2.6 | 11.6 | 10
1999-01-12 | Winter-East | 7.21 | 59.6 | 296 | 124 | 172 | 11.2 | 120
1999-01-21 | Winter-East | 7.26 | 49.7 | 186 | 80 | 106 | 11.5 | 175
1999-01-26 | Winter-East | 7.19 | 23.1 | 96 | 48 | 48 | 12 | 105
1999-02-05 | Winter-East | 7.55 | 9.27 | 36 | 16 | 20 | 11.8 | 50
1999-02-16 | Winter-East | 7.44 | 29.5 | 336 | 144 | 192 | 12.7 | 175
1999-03-09 | Winter-East | 7.31 | 128 | 520 | 210 | 310 | 11.5 | 400
1999-03-16 | Winter-East | 7.21 | 248 | 1070 | 450 | 620 | 10.8 | 1000
1999-03-23 | Winter-East | 7.36 | 13.4 | 50 | 22 | 28 | 11.7 | 80
1999-03-30 | Winter-East | 7.35 | 2.96 | 7 | 4.5 | 2.5 | 11.2 | 25
1999-04-07 | Summer-NW | 6.93 | 4.28 | 2 | 1.2 | 0.8 | 9.3 | 25
1999-04-21 | Summer-NW | 7.33 | 2.35 | 4.4 | 2 | 2.4 | 11.1 | 15
1999-04-27 | Summer-NW | 7.12 | 1.61 | 2.9 | 1.6 | 1.3 | 9.8 | 10
1999-05-06 | Summer-NW | 7.81 | 98.3 | 204 | 66 | 138 | 10.4 | 125 |  |  | very windy
1999-05-12 | Summer-NW | 7.31 | 1.76 | 4 | 1.6 | 2.4 | 10.5 | 10
1999-05-20 | Summer-NW | 7.26 | 1.25 | 1.8 | 1.6 | 0.2 |  | 10
1999-05-27 | Summer-NW | 7.22 | 3.52 | 7 | 3 | 4 | 8.7 | 20
1999-06-03 | Summer-NW | 7.35 | 24.3 | 70.6 | 38 | 32.6 | 9.3 | 60
1999-06-08 | Summer-NW | 7.24 | 19.9 | 41 | 18 | 23 | 9.2 | 60
1999-06-15 | Summer-NW | 7.19 | 46.5 | 170 | 88 | 82 | 8.5 | 175
1999-06-22 | Summer-NW | 7.46 | 8.23 | 19.6 | 8.4 | 11.2 | 7.9 | 35
1999-06-29 | Summer-NW | 6.7 | 660 | 1610 | 520 | 1090 |  | 1750
1999-08-05 | Summer-SW | 6.85 | 2.99 | 9.1 | 7.4 | 1.7 | 6.8 | 15 |  |  | Feed to lagoons off for July to repair pump. Lagoon switched and service resumed this week.
1999-08-10 | Summer-SW | 6.84 | 5.11 | 14.4 | 12.8 | 1.6 | 6.6 | 15
1999-08-19 | Summer-SW | 7.12 | 3.02 | 9.6 | 6.8 | 2.8 | 7.7 | 15
1999-08-24 | Summer-SW | 6.71 | 361 | 137 | 58 | 79 | 7.7 | 1200
1999-08-31 | Summer-SW | 6.91 | 163 | 528 | 228 | 300 | 7.8 | 300
1999-09-21 | Summer-SW | 6.85 | 38.5 | 158 | 74 | 84 | 9.9 | 125
1999-10-05 | Summer-SE | 7.03 | 2.37 | 9.6 | 6 | 3.6 | 11 | 15 |  |  | Lagoon change
1999-10-13 | Summer-SE | 7.31 | 2.67 | 2.4 | 2 | 0.4 | 10.5 | 15
1999-10-19 | Summer-SE | 7.11 | 3.32 | 9.6 | 6.8 | 2.8 | 11.5 | 15
1999-10-26 | Summer-SE | 7.14 | 2.77 | 6.4 | 3.2 | 3.2 | 10.7 | 15
1999-11-16 | Summer-SE | 6.88 | 404 | 1750 | 730 | 1020 | 12.8 | 1000
1999-11-23 | Summer-SE | 7.04 | 20.4 | 100 | 52 | 48 | 12.2 | 60
1999-12-01 | Summer-SE | 7.13 | 2.42 | 14 | 10 | 4 | 11.6 | 10
2000-12-21 | Winter-S | 7.02 | 3.84 | 11 | 7 | 4 | 12.8 | 25 |  |  | Lagoon change 06-Dec-99
2000-01-04 | Winter-S | 7.07 | 1.85 | 8 | 4.8 | 3.2 | 11.5 | 15
2000-01-11 | Winter-S | 7.16 | 2.88 | 6.6 | 3.2 | 3.4 | 12 | 15
2000-01-18 | Winter-S | 7.19 | 2.18 | 4 | 2.4 | 1.6 | 11.1 | 10
2000-01-25 | Winter-S | 7.12 | 3.03 | 5.4 | 3.2 | 2.2 | 12 | 25
2000-02-02 | Winter-S | 6.93 | 2.54 | 5.2 | 3.2 | 2 | 11 | 15
2000-02-08 | Winter-S | 6.95 | 2.74 | 6.8 | 4.4 | 2.4 | 11.6 | 20
2000-02-15 | Winter-S | 7.1 | 2.76 | 6 | 3.2 | 2.8 | 11.3 | 15
2000-02-23 | Winter-S | 6.84 | 3.52 | 5.2 | 3.8 | 1.4 | 9.2 | 25
2000-03-14 | Winter-S | 6.97 | 4.35 | 5.8 | 4.6 | 1.2 | 10.1 | 30
2000-03-21 | Winter-S | 6.93 | 385 | 1690 | 750 | 940 | 12.3 | 1400 |  |  | Lagoon switched to Summer-SW on 22-Mar-00
2000-03-28 | Summer-SW | 7.16 | 49.2 | 208 | 88 | 120 | 10.7 | 200
2000-04-04 | Summer-SW | 7.4 | 4.39 | 11.6 | 3.6 | 8 | 11.3 | 20
2000-04-11 | Summer-SW | 6.83 | 6.57 | 4.8 | 3.6 | 1.2 | 12.2 | 35
2000-04-18 | Summer-SW | 6.82 | 638 | 2400 | 990 | 1410 | 10.6 | 1500
2000-05-02 | Winter-S | 6.86 | 671 | 2460 | 920 | 1540 | 8.8 | 1250 |  |  | Lagoon switched to Winter-South on 2-may-00
2000-05-08 | Summer-SW | 7.33 | 7.94 | 9.5 | 6 | 3.5 | 9.2 | 35
2000-05-16 | Winter-S | 7.52 | 3.43 | 5.4 | 3.8 | 1.6 | 9.7 | 20
2000-05-31 | Winter-S | 7.54 | 4.36 | 0.93 | 0.72 | 0.21 | 8.7 | 25
2000-06-07 | Winter-S | 7.436 | 2.83 | 14 | 10 | 4 | 6.5 | 10
2000-06-13 | Winter-S | 7.42 | 2.86 | 6.8 | 3.6 | 3.2 | 8.1 | 10
2000-06-20 | Winter-S | 7.68 | 63 | 208 | 84 | 124 | 9 | 160
2000-06-27 | Summer-SE | 7.74 | 3.18 | 7.6 | 5.2 | 2.4 | 8.9 | 15
2000-07-05 | Summer-SE | 7.65 | 1.69 | 4.67 | 3.33 | 1.33 | 8.2 | 10
2000-07-11 | Summer-SE | 7.43 | 1.13 | 3.6 | 2.2 | 1.4 | 7.4 | 10
2000-07-18 | Summer-SE | 7.58 | 1.38 | 4.2 | 3 | 1.2 | 8 | 10
2000-07-25 | Summer-SE | 7.38 | 1.74 | 6.6 | 5.4 | 1.2 | 7.2 | 10
2000-07-31 | Summer-SE | 7.43 | 3.83 | 10.7 | 7.3 | 3.3 | 7.2 | 20
2000-08-09 | Summer-SE | 7.44 | 3.83 | 12.8 | 9.2 | 3.6 | 8.1 | 10
2000-08-15 | Summer SE | 7.07 | 583 | 184 | 75 | 109 | 7 | 1500 |  |  | lagoon changed to NE on 21-aug-00
2000-08-31 | Summer-NE | 7.52 | 2.82 | 6.4 | 5.2 | 1.2 | 8.5 | 20
2000-09-06 | Summer NE | 7.28 | 2.99 | 5 | 3.6 | 1.4 | 9 | 15
2000-09-15 | Summer NE | 7.47 | 4.5 | 8.4 | 5.6 | 2.8 | 9.4 | 35
2000-09-19 | Summer NE | 7.42 | 5.32 | 9.8 | 6 | 3.8 | 8.9 | 30
2000-10-13 | Summer NE | 7.21 | 12.5 | 70 | 20 | 20 | 10 | 60
2000-10-17 | Summer NE | 7.22 | 64.5 | 204 | 100 | 104 | 11 | 250 |  |  | lagoon changed on Oct 19, 2000
2000-10-24 | Summer NW | 7.5 | 3.84 | 8.2 | 4.8 | 3.4 | 11 | 25
2000-11-03 | Summer NW | 7.54 | 4.36 | 10.3 | 6.3 | 4 |  | 50 |  |  | Lagoon changed on Nov 9, 2000 to Winter east Lagoon.
2000-11-14 | Winter-E | 7.45 | 7.06 | 12 | 6.3 | 5.7 | 11.9 | 20
2000-11-21 | Winter-E | 7.53 | 4.94 | 9.7 | 6 | 3.7 | 11.8 | 30
2000-11-30 | Winter-E | 7.23 | 5.12 | 11.2 | 6.8 | 4.4 | 11 | 30
2000-12-05 | Winter-E | 7.16 | 4.04 | 5.6 | 3.2 | 2.4 | 12.6 | 25
2000-12-13 | Winter-E | 7.26 | 4.1 | 7.6 | 4.8 | 2.8 | 11.6 | 25
2000-12-19 | Winter-E | 7.32 | 3.68 | 6.6 | 3.8 | 2.8 | 11.3 | 20
2000-01-10 | Winter-E | 7.39 | 3.01 | 5.8 | 3.4 | 2.4 | 12.1 | 10
2000-01-16 | Winter-E | 7.48 | 2.85 | 5 | 2.8 | 2.2 | 12.9 | 15
2001-01-24 | Winter-E | 7.61 | 2.35 | 5.8 | 3.8 | 2 | 11.5 | 15
2001-02-07 | Winter-E | 7.53 | 2.91 | 5 | 3.2 | 1.8 | 11.4 | 20
2001-02-20 | Winter-E | 7.49 | 2.84 | 5.2 | 2.8 | 2.4 | 11.4 | 10
2001-03-06 | Winter-E | 7.35 | 43.4 | 188 | 68 | 120 | 12.1 | 250
2001-03-21 | Winter-E | 7.55 | 56.6 | 164 | 64 | 100 | 12 | 175
2001-03-27 | Winter-E | 7.48 | 28.7 | 128 | 64 | 64 | 11.4 | 100
2001-04-10 | Winter-E | 7 | 619 | 1840 | 920 | 920 | 10.9 | 2500 |  |  | Lagoon changed to Summer NE today
2001-04-24 | Summer-NE | 7.65 | 6.82 | 10.6 | 5.7 | 4.9 | 11.1 | 60
2001-05-08 | Summer-NE | 7.73 | 4.87 | 7.4 | 3.4 | 4 | 10.3 | 20
2001-05-15 | Summer-NE | 7.75 | 3.19 | 4 | 2.9 | 1.1 | 9.2 | 20
2001-05-23 | Summer-NE | 7.84 | 3.8 | 3.3 | 2.1 | 1.2 | 9.7 | 20
2001-05-29 | Summer-NE | 7.43 | 957 | 29.7 | 10.1 | 19.6 | 9 | 150 |  |  | high winds when sample collected
2001-06-05 | Summer-NE | 7.72 | 14.2 | 47.9 | 20 | 27.9 | 10.1 | 50
2001-06-12 | Summer-NE | 7.48 | 7.03 | 12.4 | 8.8 | 3.6 | 8.9 | 60
2001-06-19 | Summer-NE | 7.36 | 279 | 708 | 284 | 424 | 8.4 | 800 |  |  | Gene notified of carry-over.
2001-06-26 | Summer-NE | 7.21 | 669 | 2070 | 850 | 1120 | 8.2 | 1500 |  |  | Gene notified to change lagoons soon.
2001-07-10 | Summer-SE | 7.35 | 3.41 | 8.8 | 6 | 2.8 | 7.2 | 25
2001-07-17 | Summer-SE | 7.61 | 2.31 | 5.6 | 4 | 1.6 | 7.1 | 10
2001-07-24 | Summer-SE | 7.52 | 7.54 | 26 | 14 | 12 | 7.3 | 40
2001-07-31 | Summer-SE | 7.25 | 3.73 | 10.8 | 8.8 | 2 | 6.5 | 15
2001-08-08 | Summer-SE | 7.22 | 521 | 170.4 | 75.6 | 94.8 | 7.8 | 200 |  |  | Switched to Summer-NW lagoon August 9
2001-08-15 | Summer-NW | 7.36 | 3.29 | 11 | 8.6 | 2.4 | 7 | 15
2001-08-21 | Summer-NW | 7.43 | 4.65 | 14.6 | 13.2 | 1.4 | 8 | 15
2001-08-28 | Summer-NW | 7.17 | 4.19 | 21.8 | 20.2 | 1.6 | 7.2 | 20
2001-09-05 | Summer-NW | 7.03 | 11.4 | 54.4 | 51.6 | 2.8 | 2.8 | 50
2001-09-11 | Summer NW | 7.13 | 8.93 | 33.2 | 31.2 | 2 | 8.6 | 25
2001-09-18 | Summer-NW | 6.97 | 16.8 | 34 | 31.2 | 2.8 | 8.7 | 70 |  |  | Some carryover - Gene told
2001-09-25 | Summer-NW | 7.28 | 34.8 | 133 | 116 | 17 | 9 | 75 |  |  | Carryover - Notified Gene
2001-10-10 | Summer-SW | 7.19 | 11.2 | 56 | 50.8 | 5.2 | 10.1 | 50 |  |  | Switched to Summer-SW on Oct 10, 2001
2001-10-16 | Summer-SW | 7.2 | 28.1 | 103 | 88 | 15 | 11.1 | 70
2001-10-23 | Summer-SW | 7.37 | 32.4 | 139 | 93 | 46 | 11.7 | 75
2001-10-30 | Summer-SW | 7.39 | 5.63 | 20.8 | 11.6 | 9.3 | 11.7 | 15
2001-11-06 | Summer-SW | 7.33 | 59.7 | 128 | 36 | 92 | 11.6 | 200 |  |  | Gene notified of carryover.
2001-11-13 | Summer-SW | 7.23 | 263 | 800 | 272 | 528 |  | 500 |  |  | Gene notified of carryover. Switched to Winter South on November 15.
2001-11-20 | Winter-S | 7.53 | 3.46 | 6.8 | 3.8 | 3 | 12.3 | 20 |  |  | Alum - 55ppm Blowoff - 2 min
2001-11-27 | Winter-S | 7.52 | 3.64 | 10.4 | 4.8 | 5.6 | 12.6 | 15
2001-12-04 | Winter-S | 7.26 | 3.6 | 7.2 | 3.6 | 3.6 | 12.3 | 30
2001-12-11 | Winter-S | 7.29 | 3.72 | 7.2 | 3.4 | 3.8 | 12 | 25
2001-12-18 | Winter-S | 7.38 | 4.08 | 7 | 4 | 3 | 12 | 30
Average: |  | 7.3066 | 65.3972 | 179.4656 | 72.7016 | 97.099 | 9.9255 | 159.6875 | 0 | 0
| Lagoon: | Winter-South | Winter-East | Summer-NE | Summer-SE | Summer-NW | Summer-SW
| Date On: | 1997-11-02 | 1998-10-30 | 1998-06-04 | 1998-09-24 | 1999-03-31 | 1998-03-13
| Date Off: | 1998-03-13 | 1999-03-31 | 1998-09-24 | 1998-10-30 |  | 1998-06-04
| Total Days ON: | 131 | 152 | 112 | 36 |  | 83
| Total Tests for 2001: | 39 | 39 | 39 | 39 | 39 | 38 | 39 |  |  | 272

## WTP DOC Profile
BPWTP Dissolved Organic Carbon (DOC) Profile
| Actual DOC Results (mg/L) | [6 empty] | DOC % Removal
Date | Alum Dose | Raw | PreFM | FM | Channel | PreGAC/CW | CW | PreFM | FM | Channel | PreGAC/CW | CW
1998-05-28 | 60 | 8.4 | 8 | 5.6 | 5.6 |  | 4.9 | 4.7619 | 33.3333 | 33.3333 | -- | 41.6667
1998-06-04 | 55 | 7.4 | 7.2 | 4.9 | 4.6 |  | 4.6 | 2.7027 | 33.7838 | 37.8378 | -- | 37.8378
1998-07-08 | 75 | 7.2 | 7.6 | 4.4 | 4.3 | 4.1 | 1.4 | -5.5556 | 38.8889 | 40.2778 | 43.0556 | 80.5556
1998-07-15 | 75 | 7.8 | 7.4 | 5.2 | 4.2 | 4.1 | 1.6 | 5.1282 | 33.3333 | 46.1538 | 47.4359 | 79.4872
1998-07-22 | 80 | 7.6 | 7.9 | 5.2 | 4.2 | 4 | 1.8 | -3.9474 | 31.5789 | 44.7368 | 47.3684 | 76.3158
1998-07-29 | 85 | 8 | 8.1 | 4.2 | 4.3 | 4.3 | 2.5 | -1.25 | 47.5 | 46.25 | 46.25 | 68.75
1998-08-06 | 90 | 8.6 | 9.2 | 4.6 | 4.4 | 4.5 | 2.2 | -6.9767 | 46.5116 | 48.8372 | 47.6744 | 74.4186
1998-08-12 | 90 | 8.4 | 8.6 | 4.8 | 4.6 | 4.7 | 2.9 | -2.381 | 42.8571 | 45.2381 | 44.0476 | 65.4762
1998-08-19 | 90 | 9 | 9.6 | 4.7 | 4.5 | 4.5 | 1.7 | -6.6667 | 47.7778 | 50 | 50 | 81.1111
1998-08-26 | 90 | 9.2 | 9 | 4.5 | 4.5 | 4.3 | 2.2 | 2.1739 | 51.087 | 51.087 | 53.2609 | 76.087
1998-09-02 | 90 | 9.2 | 9.2 | 4.6 | 4.5 | 4.4 | 2.2 | 0 | 50 | 51.087 | 52.1739 | 76.087
1998-09-09 | 100 | 9.8 | 10.6 | 5 | 4.8 | 4.8 | 2.6 | -8.1633 | 48.9796 | 51.0204 | 51.0204 | 73.4694
1998-09-16 | 90 | 10.4 | 10.2 | 5.3 | 5.2 | 4.9 | 2.8 | 1.9231 | 49.0385 | 50 | 52.8846 | 73.0769
1998-09-23 | 80 | 9.4 | 10.4 | 4.9 | 4.7 | 4.9 | 2.9 | -10.6383 | 47.8723 | 50 | 47.8723 | 69.1489
1998-09-30 | 75 | 10 | 9.8 | 5.7 | 5.5 | 5.4 | 3.7 | 2 | 43 | 45 | 46 | 63
1998-10-07 | 55 | 9 | 9.2 | 5.8 | 5.5 | 5.7 | 3.9 | -2.2222 | 35.5556 | 38.8889 | 36.6667 | 56.6667
1998-10-14 | 50 | 10.6 | 11.4 | 5.6 | 5.5 | 5.5 | 3.9 | -7.5472 | 47.1698 | 48.1132 | 48.1132 | 63.2075
1998-10-28 | 55 | 8.8 | 9.6 | 5.6 | 5.4 | 5.4 | 3.5 | -9.0909 | 36.3636 | 38.6364 | 38.6364 | 60.2273
1998-11-04 | 65 | 8 | 8 | 5 | 5.1 | 5.2 | 3.7 | 0 | 37.5 | 36.25 | 35 | 53.75
1998-11-12 | 65 | 7.8 | 8 | 5 | 4.9 | 4.8 | 3.7 | -2.5641 | 35.8974 | 37.1795 | 38.4615 | 52.5641
1998-11-17 | 65 | 8.2 | 8.4 | 5.3 | 5.2 | 5.3 | 4 | -2.439 | 35.3659 | 36.5854 | 35.3659 | 51.2195
1998-11-25 | 55 | 7.6 | 7.6 | 5.1 | 4.9 | 4.6 | 4 | 0 | 32.8947 | 35.5263 | 39.4737 | 47.3684
1998-12-02 | 60 | 7.8 | 7.8 | 4.8 | 4.9 | 4.8 |  | 0 | 38.4615 | 37.1795 | 38.4615 | --
1998-12-09 | 55 | 8 | 8 | 5.3 | 5.2 | 5.3 |  | 0 | 33.75 | 35 | 33.75 | --
1998-12-16 | 55 | 7.8 | 7.8 | 5.5 | 5.2 | 5.1 |  | 0 | 29.4872 | 33.3333 | 34.6154 | --
1998-12-23 | 60 | 7.5 | 8 | 5.4 | 5.2 | 5.1 |  | -6.6667 | 28 | 30.6667 | 32 | --
1998-12-30 | 60 | 8 | 8.4 | 5.5 | 5.4 | 5.3 |  | -5 | 31.25 | 32.5 | 33.75 | --
1999-01-04 | 60 | 8.4 | 8.2 | 5.5 | 5.4 | 5.4 |  | 2.381 | 34.5238 | 35.7143 | 35.7143 | --
1999-01-06 | 60 | 8.2 | 8.2 | 5.5 | 5.4 | 5.5 |  | 0 | 32.9268 | 34.1463 | 32.9268 | --
1999-01-13 | 60 | 7.1 | 7 | 5.2 | 5.4 | 5.4 |  | 1.4085 | 26.7606 | 23.9437 | 23.9437 | --
1999-01-20 | 55 | 8.7 | 8.1 | 5.6 | 5.7 | 5.7 |  | 6.8966 | 35.6322 | 34.4828 | 34.4828 | --
1999-01-27 | 55 | 8.6 | 8.1 | 5.6 | 5.8 | 5.7 |  | 5.814 | 34.8837 | 32.5581 | 33.7209 | --
1999-02-03 | 55 | 8 | 8 | 5.7 | 5.7 | 5.7 |  | 0 | 28.75 | 28.75 | 28.75 | --
1999-02-10 | 55 | 8.7 | 8.8 | 5.8 | 5.8 | 5.9 |  | -1.1494 | 33.3333 | 33.3333 | 32.1839 | --
1999-02-17 | 55 | 8.1 | 8 | 5.9 | 5.7 | 5.6 |  | 1.2346 | 27.1605 | 29.6296 | 30.8642 | --
1999-02-23 | 55 | 8.5 | 7.7 | 6 | 5.5 | 5.7 |  | 9.4118 | 29.4118 | 35.2941 | 32.9412 | --
1999-03-03 | 55 | 7.6 | 7.6 | 5.4 | 5.2 | 5.2 |  | 0 | 28.9474 | 31.5789 | 31.5789 | --
1999-03-08 | 60 | 8.5 | 8.5 | 6 | 6 | 5.8 |  | 0 | 29.4118 | 29.4118 | 31.7647 | --
1999-03-15 | 60 | 8.4 | 8.4 | 5.7 | 5.7 | 5.8 |  | 0 | 32.1429 | 32.1429 | 30.9524 | --
1999-03-22 | 65 | 7.2 | 7.2 | 4.7 | 4.8 | 4.8 |  | 0 | 34.7222 | 33.3333 | 33.3333 | --
1999-03-29 | 65 | 6.8 | 6.8 | 4.7 | 4.8 | 4.8 |  | 0 | 30.8824 | 29.4118 | 29.4118 | --
1999-04-06 | 70 | 7.2 | 7.2 | 5.2 | 5 | 5 |  | 0 | 27.7778 | 30.5556 | 30.5556 | --
1999-04-12 | 70 | 7.5 | 7.7 | 5.1 | 4.9 | 5.1 |  | -2.6667 | 32 | 34.6667 | 32 | --
1999-04-19 | 65 | 8.8 | 8.6 | 5 | 4.8 | 4.8 |  | 2.2727 | 43.1818 | 45.4545 | 45.4545 | --
1999-04-26 | 65 | 8.1 | 8.7 | 4.9 | 4.8 | 4.8 |  | -7.4074 | 39.5062 | 40.7407 | 40.7407 | --
1999-05-03 | 65 | 8 | 8.6 | 4.9 | 5.1 | 4.8 |  | -7.5 | 38.75 | 36.25 | 40 | --
1999-05-10 | 65 | 7.4 | 7.8 | 4.8 | 4.6 | 4.7 |  | -5.4054 | 35.1351 | 37.8378 | 36.4865 | --
1999-05-17 | 65 | 7 | 7.2 | 4.4 | 4.3 | 4.1 |  | -2.8571 | 37.1429 | 38.5714 | 41.4286 | --
1999-05-25 | 65 | 7.8 | 8.2 | 4.9 | 4.8 | 4.9 | 1 | -5.1282 | 37.1795 | 38.4615 | 37.1795 | 87.1795
1999-05-31 | 65 | 7.8 | 8 | 5.1 | 5 | 4.9 | 1.3 | -2.5641 | 34.6154 | 35.8974 | 37.1795 | 83.3333
1999-06-07 | 75 | 7.8 | 9 | 5.1 | 5.1 | 4.8 | 1.3 | -15.3846 | 34.6154 | 34.6154 | 38.4615 | 83.3333
1999-06-14 | 80 | 8.4 | 8.9 | 4.9 | 5 | 5 | 1.6 | -5.9524 | 41.6667 | 40.4762 | 40.4762 | 80.9524
1999-06-21 | 80 | 9 | 9.4 |  |  | 5 | 1.8 | -4.4444 | -- | -- | 44.4444 | 80
1999-06-28 | 75 | 9 | 9 |  |  | 4.9 | 1.7 | 0 | -- | -- | 45.5556 | 81.1111
1999-07-05 | 65 | 8.8 | 8.6 |  |  | 5 | 2.3 | 2.2727 | -- | -- | 43.1818 | 73.8636
1999-07-12 | 70 | 9 | 9.8 |  |  | 5.4 | 2.2 | -8.8889 | -- | -- | 40 | 75.5556
1999-07-19 | 78 | 11.2 |  |  |  | 5.4 | 2.8 | -- | -- | -- | 51.7857 | 75
1999-07-26 | 85 | 15 | 17.6 |  |  | 5.9 | 3.1 | -17.3333 | -- | -- | 60.6667 | 79.3333
1999-08-03 | 85 | 12 | 12.4 |  |  | 5.4 | 2.6 | -3.3333 | -- | -- | 55 | 78.3333
1999-08-09 | 85 | 12.8 | 12.4 |  |  | 5.8 | 2.9 | 3.125 | -- | -- | 54.6875 | 77.3438
1999-08-16 | 100 | 13 | 10.5 |  |  | 5.7 | 2.5 | 19.2308 | -- | -- | 56.1538 | 80.7692
1999-08-23 | 100 | 12 | 12 |  |  | 5.4 | 2.5 | 0 | -- | -- | 55 | 79.1667
1999-08-30 | 100 | 11.6 | 12 |  |  | 5.5 | 2.8 | -3.4483 | -- | -- | 52.5862 | 75.8621
1999-09-08 | 100 | 10.8 | 11.2 |  |  | 5.8 | 3.2 | -3.7037 | -- | -- | 46.2963 | 70.3704
1999-09-13 | 100 | 11.2 | 11.2 |  |  | 5.3 | 3 | 0 | -- | -- | 52.6786 | 73.2143
1999-09-20 | 100 | 12.4 | 13.6 |  |  | 5.8 | 3.9 | -9.6774 | -- | -- | 53.2258 | 68.5484
1999-09-28 | 100 | 13 | 12.7 |  |  | 5.5 | 3.9 | 2.3077 | -- | -- | 57.6923 | 70
1999-10-04 | 100 | 12.8 | 13.2 |  |  | 5.5 | 4 | -3.125 | -- | -- | 57.0312 | 68.75
1999-10-12 | 92 | 12.4 | 14 |  |  | 6 | 4.2 | -12.9032 | -- | -- | 51.6129 | 66.129
1999-10-18 | 87 | 11.6 | 12 |  |  | 5.8 | 4.2 | -3.4483 | -- | -- | 50 | 63.7931
1999-10-25 | 87 | 11.2 | 12 |  |  | 5.7 | 4.4 | -7.1429 | -- | -- | 49.1071 | 60.7143
1999-11-01 | 88 | 11.2 | 11.6 |  |  | 5.9 | 4.3 | -3.5714 | -- | -- | 47.3214 | 61.6071
1999-11-08 | 92 | 12.6 | 13.6 |  |  | 5.6 | 4.2 | -7.9365 | -- | -- | 55.5556 | 66.6667
1999-11-15 | 88 | 12.4 | 13.6 |  |  |  | 5.9 | -9.6774 | -- | -- | -- | 52.4194
1999-11-22 | 82 | 11.6 | 10.8 |  |  |  | 5.4 | 6.8966 | -- | -- | -- | 53.4483
1999-11-29 | 82 | 11.2 | 11.2 |  |  |  | 5.6 | 0 | -- | -- | -- | 50
1999-12-06 | 82 | 11.1 | 11.3 |  |  |  | 5.8 | -1.8018 | -- | -- | -- | 47.7477
1999-12-13 | 82 | 13.6 | 12.7 |  |  |  | 5.8 | 6.6176 | -- | -- | -- | 57.3529
1999-12-20 | 90 | 11.9 | 12.3 |  |  |  | 6.3 | -3.3613 | -- | -- | -- | 47.0588
1999-12-27 | 88 | 12.6 | 12.6 |  |  |  | 6 | 0 | -- | -- | -- | 52.381
2000-01-03 | 88 | 12.2 | 12.1 |  |  |  | 6.4 | 0.81967 | -- | -- | -- | 47.541
2000-01-10 | 87 | 12.6 | 11.7 |  |  |  | 6.3 | 7.1429 | -- | -- | -- | 50
2000-01-17 | 87 | 11.9 | 12.2 |  |  |  | 5.8 | -2.521 | -- | -- | -- | 51.2605
2000-01-24 | 87 | 12.5 |  | 6 | 6.5 |  | 5.9 | -- | 52 | 48 | -- | 52.8
2000-02-01 | 95 | 12.7 |  | 6.4 | 6.5 |  | 6.1 | -- | 49.6063 | 48.8189 | -- | 51.9685
2000-02-07 | 95 | 12.1 |  | 6.2 | 6.4 |  | 6.4 | -- | 48.7603 | 47.1074 | -- | 47.1074
2000-02-14 | 95 | 12.6 |  | 6.7 | 6.6 |  | 6.3 | -- | 46.8254 | 47.619 | -- | 50
2000-02-22 | 95 | 11.8 | 11.7 |  |  |  | 6.1 | 0.84746 | -- | -- | -- | 48.3051
2000-02-29 | 95 | 12.4 |  |  | 6.2 |  | 6 | -- | -- | 50 | -- | 51.6129
2000-03-07 | 95 | 11.5 |  | 6 |  |  | 6 | -- | 47.8261 | -- | -- | 47.8261
2000-03-13 | 95 | 11.6 |  | 6.1 | 6.2 |  | 5.9 | -- | 47.4138 | 46.5517 | -- | 49.1379
2000-03-20 | 95 | 12.3 |  | 6.5 | 6.5 |  | 6.5 | -- | 47.1545 | 47.1545 | -- | 47.1545
2000-03-27 | 95 | 12.2 |  | 6.5 | 6.3 |  | 6.3 | -- | 46.7213 | 48.3607 | -- | 48.3607
2000-04-03 | 95 | 10.3 |  | 4.9 | 4.9 |  | 4.8 | -- | 52.4272 | 52.4272 | -- | 53.3981
2000-04-10 | 92 | 10.4 |  | 5.3 | 5 |  | 5.1 | -- | 49.0385 | 51.9231 | -- | 50.9615
2000-04-17 | 82 | 8.3 |  | 5.3 | 5 |  | 5.1 | -- | 36.1446 | 39.759 | -- | 38.5542
2000-04-25 | 82 | 9.3 |  | 5.3 | 5.1 |  | 5.3 | -- | 43.0108 | 45.1613 | -- | 43.0108
2000-05-01 | 86 | 9.2 |  | 5.1 | 4.9 |  | 5.2 | -- | 44.5652 | 46.7391 | -- | 43.4783
2000-05-08 | 86 | 8.4 |  | 4.9 | 5.3 |  | 5.1 | -- | 41.6667 | 36.9048 | -- | 39.2857
2000-05-15 | 86 | 8 |  | 4.8 | 4.8 |  | 4.8 | -- | 40 | 40 | -- | 40
2000-05-23 | 74 | 8.6 |  | 5.1 | 5 | 5.2 | 1.3 | -- | 40.6977 | 41.8605 | 39.5349 | 84.8837
2000-05-29 | 74 | 8.6 |  | 5.1 | 5 | 5.2 | 1.3 | -- | 40.6977 | 41.8605 | 39.5349 | 84.8837
2000-06-05 | 72 | 7 |  | 5 | 4.6 | 4.7 | 1 | -- | 28.5714 | 34.2857 | 32.8571 | 85.7143
2000-06-12 | 70 | 6.6 |  | 4.4 | 4.3 | 4.5 | 1 | -- | 33.3333 | 34.8485 | 31.8182 | 84.8485
2000-06-19 | 65 | 8.7 |  |  | 4.8 | 4.6 | 1 | -- | -- | 44.8276 | 47.1264 | 88.5057
2000-06-26 | 80 | 7.7 |  |  | 4.9 | 4.5 | 1.2 | -- | -- | 36.3636 | 41.5584 | 84.4156
2000-07-03 | 85 | 8.4 |  |  | 4.5 | 4.4 | 1.1 | -- | -- | 46.4286 | 47.619 | 86.9048
2000-07-10 | 85 | 8.8 |  |  | 4.8 | 4.5 | 1.5 | -- | -- | 45.4545 | 48.8636 | 82.9545
2000-07-17 | 85 | 10.2 |  |  | 5 | 5.2 | 2.7 | -- | -- | 50.9804 | 49.0196 | 73.5294
2000-07-24 | 80 | 8.4 |  |  | 4.7 | 4.7 | 2.2 | -- | -- | 44.0476 | 44.0476 | 73.8095
2000-07-31 | 75 | 8.7 |  |  | 5 | 5.1 | 2.8 | -- | -- | 42.5287 | 41.3793 | 67.8161
2000-08-08 | 75 | 8.8 |  |  | 4.7 | 4.7 | 2.5 | -- | -- | 46.5909 | 46.5909 | 71.5909
2000-08-14 | 75 | 8.4 |  |  | 5.1 | 5.3 | 2.9 | -- | -- | 39.2857 | 36.9048 | 65.4762
2000-08-21 | 75 | 8.6 |  |  | 4.8 | 4.7 | 1.9 | -- | -- | 44.186 | 45.3488 | 77.907
2000-08-28 | 85 | 9 |  |  | 4.6 | 4.6 | 2.4 | -- | -- | 48.8889 | 48.8889 | 73.3333
2000-09-05 | 85 | 8.9 |  |  | 4.6 | 4.5 | 2.7 | -- | -- | 48.3146 | 49.4382 | 69.6629
2000-09-11 | 85 | 8.4 |  |  | 4.4 | 4.6 | 2.8 | -- | -- | 47.619 | 45.2381 | 66.6667
2000-09-18 | 85 | 8 |  |  | 4.4 | 4.3 | 2.9 | -- | -- | 45 | 46.25 | 63.75
2000-09-25 | 90 | 7 |  |  | 4.1 | 4.2 | 2.5 | -- | -- | 41.4286 | 40 | 64.2857
2000-10-03 | 80 | 8 | 7.4 |  | 4.4 | 4.1 | 2.9 | 7.5 | -- | 45 | 48.75 | 63.75
2000-10-10 | 65 | 8.6 |  |  | 5 | 4.8 | 3.6 | -- | -- | 41.8605 | 44.186 | 58.1395
2000-10-16 | 65 | 8.2 |  |  | 4.8 | 4.6 | 3.6 | -- | -- | 41.4634 | 43.9024 | 56.0976
2000-10-23 | 65 | 8.1 |  |  | 4.8 | 4.7 | 3.6 | -- | -- | 40.7407 | 41.9753 | 55.5556
2000-10-31 | 60 | 7.8 |  |  | 4.5 | 4.4 | 3.6 | -- | -- | 42.3077 | 43.5897 | 53.8462
2000-11-07 | 55 | 7.6 |  |  | 4.5 | 4.4 | 3.6 | -- | -- | 40.7895 | 42.1053 | 52.6316
2000-11-13 | 60 | 7.6 |  |  | 4.6 | 4.5 | 3.9 | -- | -- | 39.4737 | 40.7895 | 48.6842
2000-11-20 | 60 | 8 |  |  | 4.6 |  | 4.6 | -- | -- | 42.5 | -- | 42.5
2000-11-27 | 57.5 | 8 |  |  | 4.9 |  | 4.8 | -- | -- | 38.75 | -- | 40
2000-12-04 | 60 | 7.6 |  |  | 4.6 |  | 4.7 | -- | -- | 39.4737 | -- | 38.1579
2000-12-11 | 55 | 7.9 |  |  |  |  | 5 | -- | -- | -- | -- | 36.7089
2000-12-21 | 60 | 8.5 |  |  | 5.4 |  | 5.2 | -- | -- | 36.4706 | -- | 38.8235
2001-01-03 | 60 | 8.2 |  |  | 5.3 |  | 5.3 | -- | -- | 35.3659 | -- | 35.3659
2001-01-08 | 60 | 8.9 |  |  | 5.6 |  | 5.5 | -- | -- | 37.0787 | -- | 38.2022
2001-01-15 | 60 | 8.2 |  |  | 5.6 |  | 5.4 | -- | -- | 31.7073 | -- | 34.1463
2001-01-22 | 60 | 8.3 |  |  | 5.5 |  | 5.4 | -- | -- | 33.7349 | -- | 34.9398
2001-01-31 | 60 | 7.9 |  |  | 5.4 |  | 5.3 | -- | -- | 31.6456 | -- | 32.9114
2001-02-06 | 60 | 8.2 |  |  | 5.4 |  | 5.4 | -- | -- | 34.1463 | -- | 34.1463
2001-02-13 | 60 | 7.8 |  |  | 5.5 |  | 5.6 | -- | -- | 29.4872 | -- | 28.2051
2001-02-19 | 60 | 8 |  |  | 5.4 |  | 5.5 | -- | -- | 32.5 | -- | 31.25
2001-02-27 | 60 | 8.1 |  |  | 5.5 |  | 5.5 | -- | -- | 32.0988 | -- | 32.0988
2001-03-05 | 65 | 8.1 |  |  | 5.7 |  | 5.6 | -- | -- | 29.6296 | -- | 30.8642
2001-03-12 | 65 | 8.2 |  |  | 5.4 |  | 5.4 | -- | -- | 34.1463 | -- | 34.1463
2001-03-19 | 65 | 7.5 |  |  | 5.3 |  | 5.4 | -- | -- | 29.3333 | -- | 28
2001-03-26 | 65 | 7.1 |  |  | 5.2 |  | 5.2 | -- | -- | 26.7606 | -- | 26.7606
2001-04-04 | 72.5 | 7.7 |  |  | 5.3 |  | 5.3 | -- | -- | 31.1688 | -- | 31.1688
2001-04-09 | 72.5 | 7.6 |  |  | 4.8 |  | 4.4 | -- | -- | 36.8421 | -- | 42.1053 | PAC ON
2001-04-18 | 73 | 7.6 |  |  | 5 |  | 4.9 | -- | -- | 34.2105 | -- | 35.5263
2001-04-23 | 73 | 8 |  |  | 5.2 |  | 5.2 | -- | -- | 35 | -- | 35
2001-04-30 | 73 | 6.6 |  |  | 3.3 |  | 3.3 | -- | -- | 50 | -- | 50
2001-05-07 | 70 | 7 |  |  | 4.3 |  | 4.1 | -- | -- | 38.5714 | -- | 41.4286
2001-05-14 | 70 | 6.8 |  |  | 4.1 |  | 4.3 | -- | -- | 39.7059 | -- | 36.7647
2001-05-22 | 65 | 6.5 |  |  | 4.3 |  | 4.1 | -- | -- | 33.8462 | -- | 36.9231
2001-05-28 | 65 | 6.8 |  |  | 4.7 |  | 4.5 | -- | -- | 30.8824 | -- | 33.8235
2001-06-04 | 65 | 7.7 |  |  | 4.5 | 4.3 | 1.1 | -- | -- | 41.5584 | 44.1558 | 85.7143 | GAC's on May 31
2001-06-11 | 65 | 7.7 |  |  | 4.6 | 4.7 | 0.9 | -- | -- | 40.2597 | 38.961 | 88.3117
2001-06-18 | 70 | 7.1 |  |  | 4.6 | 4.5 | 1 | -- | -- | 35.2113 | 36.6197 | 85.9155
2001-06-25 | 70 | 8.2 |  |  | 4.7 | 4.7 | 1.2 | -- | -- | 42.6829 | 42.6829 | 85.3659
2001-07-02 | 70 | 7.7 |  |  | 4.8 | 4.8 | 1.4 | -- | -- | 37.6623 | 37.6623 | 81.8182
2001-07-09 | 70 | 7.6 |  |  | 4.7 | 4.6 | 1.6 | -- | -- | 38.1579 | 39.4737 | 78.9474
2001-07-16 | 70 | 7.4 |  |  | 4.5 | 4.4 | 1.6 | -- | -- | 39.1892 | 40.5405 | 78.3784
2001-07-23 | 70 | 7.6 |  |  | 4.9 | 4.8 | 2.1 | -- | -- | 35.5263 | 36.8421 | 72.3684
2001-07-30 | 70 | 7.6 |  |  | 4.4 | 4.3 | 2 | -- | -- | 42.1053 | 43.4211 | 73.6842
2001-08-07 | 70 | 7.4 |  |  | 4.5 | 4.6 | 2.4 | -- | -- | 39.1892 | 37.8378 | 67.5676
2001-08-13 | 80 | 7 |  |  | 4.1 | 4 | 2.2 | -- | -- | 41.4286 | 42.8571 | 68.5714
2001-08-20 | 80 | 7.6 |  |  | 4.3 | 4.4 | 2.4 | -- | -- | 43.4211 | 42.1053 | 68.4211
2001-08-27 | 90 | 7.4 |  |  | 4.3 | 4.3 | 2.4 | -- | -- | 41.8919 | 41.8919 | 67.5676
2001-09-04 | 90 | 7.2 |  |  | 4 | 4 | 2.5 | -- | -- | 44.4444 | 44.4444 | 65.2778
2001-09-10 | 90 | 7.8 |  |  | 4.4 | 4.3 | 2.6 | -- | -- | 43.5897 | 44.8718 | 66.6667
2001-09-17 | 80 | 8.4 |  |  | 5.4 | 5 | 3.1 | -- | -- | 35.7143 | 40.4762 | 63.0952
2001-09-24 | 80 | 8 |  |  | 4.9 | 4.9 | 3.2 | -- | -- | 38.75 | 38.75 | 60
2001-10-01 | 82 | 7.6 |  |  | 4.8 | 4.8 | 3.2 | -- | -- | 36.8421 | 36.8421 | 57.8947
2001-10-09 | 82 | 7.6 |  |  | 4.9 | 4.8 | 3.2 | -- | -- | 35.5263 | 36.8421 | 57.8947
2001-10-15 | 100 | 7.6 |  |  | 4.2 | 4.1 | 2.8 | -- | -- | 44.7368 | 46.0526 | 63.1579
2001-10-22 | 85 | 7 |  |  | 4.3 | 4.3 | 2.7 | -- | -- | 38.5714 | 38.5714 | 61.4286
2001-10-29 | 85 | 6.8 |  |  | 4.1 | 4 | 2.9 | -- | -- | 39.7059 | 41.1765 | 57.3529
2001-11-05 | 75 | 6.8 |  |  | 4.2 | 4.2 | 3.2 | -- | -- | 38.2353 | 38.2353 | 52.9412
2001-11-12 | 80 | 6 |  |  | 4 | 3.9 | 3.2 | -- | -- | 33.3333 | 35 | 46.6667
2001-11-19 | 60 | 6.7 |  |  | 4.3 | 4.2 | 3.6 | -- | -- | 35.8209 | 37.3134 | 46.2687
2001-11-26 | 55 | 6.6 |  |  | 4.4 |  | 4.4 | -- | -- | 33.3333 | -- | 33.3333
2001-12-03 | 60 | 6.3 |  |  | 4 |  | 4.1 | -- | -- | 36.5079 | -- | 34.9206
2001-12-10 | 55 | 6.6 |  |  | 4.4 |  | 4.3 | -- | -- | 33.3333 | -- | 34.8485
2001-12-17 | 55 | 6.4 |  |  | 4.5 |  | 4.4 | -- | -- | 29.6875 | -- | 31.25
2001-12-31 | 65 | 6.6 |  |  | 4.7 |  | 4.6 | -- | -- | 28.7879 | -- | 30.303
2001 Average | 70.25 | 7.4442 | #DIV/0! | #DIV/0! | 4.7346 | 4.436 | 3.6712 | #DIV/0! | #DIV/0! | 36.4051 | 40.1451 | 50.5713
2000 Average | 79.5196 | 9.3529 | 11.02 | 5.5579 | 5.0578 | 4.6538 | 3.9647 | 2.7578 | 44.0242 | 43.7813 | 43.3584 | 58.5803
1999 Average: | 76 | 9.917 | 10.0731 | 5.264 | 5.212 | 5.3522 | 3.5156 | -1.7297 | 33.6424 | 34.2903 | 42.2199 | 69.4168
1998 Average: | 71.2963 | 8.5 | 8.7037 | 5.0926 | 4.9 | 4.84 | 3.0318 | -2.3118 | 39.5273 | 41.8785 | 42.9335 | 64.6133
Min: | 50 | 6 | 6.8 | 4.2 | 3.3 | 3.9 | 0.9 | -17.3333 | 26.7606 | 23.9437 | 23.9437 | 26.7606
Max: | 100 | 15 | 17.6 | 6.7 | 6.6 | 6 | 6.5 | 19.2308 | 52.4272 | 52.4272 | 60.6667 | 88.5057
| Total Channel Tests for 2001: |  |  |  | 51

## CW THMFP
Clearwell - SDSTHMC
Date |  |  | pH |  | DOC (mg/L) |  | Trihalomethanes (µg/L) | [9 empty] | Chlorine (mg/L)
Collected | Initial (I) Analyzed | Final (F) Analyzed | I pH | F pH | I DOC | F DOC | I CHCl3 | F CHCl3 | I CHCl2Br | F CHCl2Br | I CHBr2Cl | F CHBr2Cl | I CHBr3 | F CHBr3 | I Total | F Total | I Free | F Free | I Combined | F Combined
1999-04-19 | 1999-04-19 | 1999-04-26 | 7.1 | 7.02 | 4.8 |  | 57 | 81 | 8 | 16 | 1 | 1 | 0 | 0 | 66 | 98 | 0.85 | 0 | 0.2 | 0
1999-04-26 | 1999-04-26 | 1999-05-03 | 6.99 | 7.16 | 4.8 |  | 62 | 103 | 10 | 20 | 1 | 1 | 0 | 0 | 73 | 124 | 1 | 0 | 0.1 | 0
1999-05-03 | 1999-05-03 | 1999-05-10 | 7.05 | 7.16 | 4.8 |  | 70 | 111 | 14 | 21 | 1 | 2 | 0 | 0 | 85 | 134 | 1.1 | 0 | 0.15 | 0
1999-05-17 | 1999-05-17 | 1999-05-25 | 7.1 | 7 | 4.1 |  | 58 | 104 | 15 | 25 | 1 | 2 | 0 | 0 | 74 | 131 | 1.15 | 0 | 0.25 | 0.1
1999-05-25 | 1999-05-25 | 1999-06-01 | 7.92 | 8.14 | 1 |  | 3 | 12 | 0 | 6 | 0 | 4 | 0 | 2 | 3 | 24 | 1.25 | 0.85 | 0 | 0
1999-05-31 | 1999-05-31 | 1999-06-07 | 7.37 | 7.25 | 1.3 |  | 3 | 6 | 0 | 4 | 0 | 4 | 0 | 1 | 3 | 15 | 1.25 | 0.9 | 0 | 0
1999-06-07 | 1999-06-07 | 1999-06-14 | 7.33 | 7.53 | 1.3 |  | 3 | 5 | 0 | 3 | 0 | 2 | 0 | 1 | 3 | 11 | 1 | 0.6 | 0 | 0
1999-06-14 | 1999-06-14 | 1999-06-21 | 7.32 | 7.39 | 1.6 |  | 7 | 12 | 1 | 7 | 0 | 5 | 0 | 0 | 8 | 24 | 1.15 | 0.6 | 0 | 0
1999-06-21 | 1999-06-21 | 1999-06-28 | 7.28 | 7.11 | 1.9 |  | 11 | 16 | 1 | 8 | 0 | 4 | 0 | 1 | 12 | 29 | 1.25 | 0.65 | 0 | 0
1999-06-28 | 1999-06-28 | 1999-07-05 | 7.21 | 7.08 | 1.8 |  | 17 | 23 | 1 | 9 | 0 | 4 | 0 | 1 | 18 | 37 | 1.2 | 0.6 | 0 | 0
1999-07-05 | 1999-07-05 | 1999-07-12 | 7.28 | 7.28 | 2.3 |  | 26 | 38 | 3 | 12 | 0 | 6 | 0 | 1 | 29 | 57 | 1.05 | 0.3 | 0 | 0
1999-07-12 | 1999-07-12 | 1999-07-19 | 7.14 | 7.04 | 2.2 |  | 30 | 43 | 3 | 13 | 0 | 5 | 0 | 1 | 33 | 62 | 1.15 | 0.4 | 0 | 0
1999-07-19 | 1999-07-19 | 1999-07-26 | 7.19 | 7.06 | 1.6 |  | 45 | 59 | 6 | 15 | 0 | 5 | 0 | 0 | 51 | 79 | 1.2 | 0.3 | 0 | 0
1999-07-26 | 1999-07-26 | 1999-08-03 | 7.05 | 6.97 | 3.1 |  | 49 | 63 | 6 | 17 | 1 | 6 | 0 | 1 | 56 | 87 | 1.2 | 0.2 | 0.1 | 0
1999-08-03 | 1999-08-03 | 1999-08-09 | 6.94 | 6.81 | 2.6 |  | 55 | 57 | 10 | 10 | 1 | 1 | 0 | 0 | 66 | 68 | 1.1 | 0.05 | 0.1 | 0
1999-08-09 | 1999-08-09 | 1999-08-16 | 6.86 | 6.83 | 2.9 |  | 58 | 77 | 14 | 28 | 1 | 8 | 0 | 1 | 73 | 114 | 1.15 | 0.1 | 0.05 | 0
1999-08-16 | 1999-08-16 | 1999-08-23 | 7.11 | 7.23 | 2.5 |  | 45 | 51 | 10 | 16 | 1 | 6 | 0 | 0 | 56 | 73 | 1 | 0.1 | 0.1 | 0
1999-08-23 | 1999-08-23 | 1999-08-30 | 6.93 | 6.9 | 2.1 |  | 52 | 60 | 12 | 24 | 1 | 8 | 0 | 2 | 65 | 94 | 1.1 | 0.15 | 0.1 | 0.1
1999-09-27 | 1999-09-27 | 1999-10-04 | 7.18 | 6.9 | 3.9 |  | 45 | 64 | 14 | 27 | 1 | 7 | 0 | 2 | 60 | 100 | 1.1 | 0.15 | 0.05 | 0
1999-10-04 | 1999-10-04 | 1999-10-12 | 6.95 | 7 | 4 |  | 41 | 62 | 12 | 27 | 1 | 6 | 0 | 0 | 54 | 95 | 1.25 | 0.05 | 0.1 | 0
1999-10-12 | 1999-10-12 | 1999-10-19 | 7.1 |  | 4.2 |  | 33 | 47 | 14 | 24 | 1 | 7 | 0 | 1 | 48 | 79 | 1.2 | 0.05 | 0.1 | 0
1999-10-19 | 1999-10-19 | 1999-10-26 | 6.98 | 6.94 | 4.2 |  | 31 | 51 | 14 | 28 | 1 | 7 | 0 | 1 | 46 | 87 | 1.1 | 0.05 | 0.1 | 0
1999-10-25 | 1999-10-25 | 1999-11-01 | 6.99 | 7.09 | 4.4 |  | 28 | 44 | 14 | 25 | 1 | 6 | 0 | 0 | 43 | 75 | 1.2 | 0.05 | 0.15 | 0
1999-11-01 | 1999-11-01 | 1999-11-08 | 6.74 | 6.71 | 4.3 |  | 28 | 51 | 15 | 31 | 2 | 8 | 0 | 1 | 45 | 91 | 1.25 | 0.05 | 0.1 | 0
1999-11-08 | 1999-11-08 | 1999-11-15 | 6.65 | 6.83 | 4.2 |  | 26 | 46 | 14 | 29 | 2 | 7 | 0 | 1 | 42 | 83 | 1.15 | 0.05 | 0.15 | 0
1999-11-15 | 1999-11-15 | 1999-11-22 | 6.68 | 6.69 | 5.9 |  | 19 | 44 | 12 | 29 | 3 | 7 | 0 | 0 | 34 | 80 | 1.15 | 0 | 0.25 | 0.1 | Contactor's off 12-Nov-99
1999-11-22 | 1999-11-22 | 1999-11-29 | 6.98 | 7 | 5.4 |  | 20 | 52 | 13 | 29 | 3 | 6 | 0 | 0 | 36 | 87 | 0.95 | 0 | 0.35 | 0.05
1999-11-29 | 1999-11-29 | 1999-12-06 | 6.9 | 7 | 5.6 |  | 17 | 39 | 10 | 25 | 2 | 5 | 0 | 0 | 29 | 69 | 1.1 | 0 | 0.25 | 0.05
1999-12-06 | 1999-12-06 | 1999-12-13 | 7.09 | 7.21 | 5.8 |  | 19 | 57 | 14 | 34 | 4 | 8 | 0 | 0 | 37 | 99 | 1.1 | 0 | 0.3 | 0
1999-12-13 | 1999-12-13 | 1999-12-20 | 6.93 | 7.04 | 5.8 |  | 19 | 40 | 13 | 26 | 3 | 6 | 0 | 0 | 35 | 72 | 1.15 | 0 | 0.2 | 0.05
1999-12-20 | 1999-12-20 | 1999-12-27 | 7.04 | 7.22 | 6.3 |  | 22 | 43 | 16 | 27 | 4 | 6 | 0 | 0 | 42 | 76 | 1.1 | 0 | 0.3 | 0.1
1999-12-27 | 1999-12-27 | 2000-01-03 | 7.06 | 7.18 | 6 |  | 22 | 46 | 15 | 30 | 4 | 7 | 0 | 0 | 41 | 83 | 1.15 | 0 | 0.3 | 0.1
2000-01-03 | 2000-01-03 | 2000-01-10 | 6.97 | 6.97 | 6.4 |  | 21 | 57 | 15 | 31 | 4 | 7 | 0 | 0 | 40 | 95 | 1.2 | 0 | 0.3 | 0.1
2000-01-10 | 2000-01-10 | 2000-01-17 | 6.94 | 7.06 | 6.3 |  | 21 | 53 | 15 | 32 | 4 | 8 | 0 | 0 | 40 | 93 | 1.15 | 0 | 0.3 | 0
2000-01-17 | 2000-01-17 | 2000-01-24 | 6.78 | 6.93 | 5.8 |  | 19 | 46 | 12 | 30 | 3 | 6 | 0 | 0 | 34 | 82 | 1.15 | 0 | 0.25 | 0.1 | Jan 17 - chlorine on at channel and off at LPS
2000-01-19 | 2000-01-19 | 2000-01-26 | 6.99 | 6.91 | 5.9 |  | 11 | 32 | 7 | 28 | 2 | 10 | 0 | 1 | 20 | 71 | 1.25 | 0 | 0.2 | 0.15
2000-01-24 | 2000-01-24 | 2000-01-31 | 6.88 | 6.81 | 5.9 |  | 9 | 28 | 5 | 25 | 2 | 9 | 0 | 0 | 16 | 62 | 1.15 | 0.05 | 0.2 | 0
2000-01-26 | 2000-01-26 | 2000-02-02 | 6.96 | 7.08 | 6.4 |  | 11 | 39 | 9 | 31 | 3 | 10 | 0 | 0 | 23 | 80 | 1.15 | 0 | 0.25 | 0.1
2000-01-31 | 2000-01-31 | 2000-02-06 | 6.75 | 6.99 | 5.9 |  | 8 | 32 | 4 | 29 | 2 | 11 | 0 | 1 | 14 | 73 | 1.1 | 0 | 0.2 | 0
2000-02-02 | 2000-02-02 | 2000-02-09 | 6.85 | 6.96 | 6.2 |  | 11 | 26 | 6 | 26 | 2 | 10 | 0 | 1 | 19 | 63 | 0.9 | 0 | 0.15 | 0
2000-02-07 | 2000-02-07 | 2000-02-15 | 6.78 | 6.82 | 6.4 |  | 9 | 29 | 5 | 27 | 2 | 10 | 0 | 1 | 16 | 67 | 1.05 | 0 | 0.2 | 0
2000-02-09 | 2000-02-09 | 2000-02-16 | 7.09 | 7.11 | 6.2 |  | 10 | 26 | 8 | 24 | 3 | 8 | 0 | 1 | 21 | 59 | 1 | 0 | 0.2 | 0.1
2000-02-14 | 2000-02-14 | 2000-02-21 | 6.85 | 6.84 | 6.3 |  | 10 | 30 | 5 | 28 | 2 | 11 | 0 | 1 | 17 | 70 | 1.05 | 0 | 0.25 | 0
2000-02-16 | 2000-02-16 | 2000-02-23 | 6.81 | 6.86 | 6.5 |  | 10 | 38 | 8 | 32 | 2 | 11 | 0 | 1 | 20 | 82 | 1.35 | 0 | 0.3 | 0.1 | Feb 21 - chlorine off at channel and started at LPS
2000-02-22 | 2000-02-22 | 2000-02-29 | 6.87 | 6.97 | 6.1 |  | 18 | 46 | 12 | 34 | 3 | 9 | 0 | 1 | 33 | 90 | 1.1 | 0 | 0.3 | 0
2000-02-28 | 2000-02-28 | 2000-03-06 | 6.81 | 6.93 | 6 |  | 19 | 52 | 13 | 34 | 4 | 9 | 0 | 0 | 36 | 95 | 1.1 | 0 | 0.3 | 0.1
2000-03-06 | 2000-03-06 | 2000-03-13 | 6.89 | 6.96 | 6 |  | 22 | 50 | 14 | 34 | 4 | 9 | 0 | 1 | 40 | 94 | 0.95 | 0 | 0.3 | 0.1
2000-03-13 | 2000-03-13 | 2000-03-20 | 6.94 | 7.07 | 5.9 |  | 26 | 54 | 17 | 35 | 5 | 10 | 0 | 1 | 48 | 100 | 0.8 | 0 | 0.3 | 0.1
2000-03-20 | 2000-03-20 | 2000-03-27 | 7.03 | 7.35 | 6.5 |  | 28 | 58 | 19 | 34 | 6 | 9 | 0 | 0 | 53 | 101 | 0.95 | 0 | 0.35 | 0.1 | pH meter was changed on Mar 24
2000-03-27 | 2000-03-27 | 2000-04-03 | 7.22 | 7.36 | 6.3 |  | 24 | 65 | 16 | 35 | 4 | 9 | 0 | 0 | 44 | 109 | 1.25 | 0 | 0.3 | 0
2000-04-03 | 2000-04-03 | 2000-04-10 | 7.07 | 7.02 | 4.8 |  | 15 | 38 | 9 | 25 | 3 | 7 | 0 | 1 | 27 | 71 | 1.05 | 0 | 0.25 | 0.1
2000-04-10 | 2000-04-10 | 2000-04-17 | 7.08 | 7.12 | 5.1 |  | 16 | 48 | 9 | 26 | 3 | 6 | 0 | 0 | 28 | 80 | 1.1 | 0 | 0.25 | 0
2000-04-17 | 2000-04-17 | 2000-04-25 | 7.2 | 7.28 | 5.1 |  | 20 | 55 | 11 | 28 | 3 | 6 | 0 | 0 | 34 | 89 | 1.15 | 0 | 0.25 | 0
2000-04-25 | 2000-04-25 | 2000-05-02 | 7.21 | 7.25 | 5.3 |  | 20 | 47 | 14 | 26 | 4 | 6 | 0 | 0 | 38 | 79 | 1.1 | 0 | 0.25 | 0.1
2000-05-01 | 2000-05-01 | 2000-05-08 | 7.25 | 7.17 | 5.2 |  | 22 | 51 | 13 | 26 | 3 | 5 | 0 | 0 | 38 | 82 | 1.05 | 0 | 0.25 | 0
2000-05-08 | 2000-05-08 | 2000-05-15 | 7.31 | 7.12 | 5.1 |  | 22 | 48 | 15 | 25 | 4 | 6 | 0 | 0 | 41 | 79 | 1 | 0 | 0.15 | 0.1
2000-05-15 | 2000-05-15 | 2000-05-23 | 7.27 | 7.2 | 4.8 |  | 23 | 50 | 14 | 25 | 3 | 5 | 0 | 0 | 40 | 80 | 1 | 0 | 0.1 | 0
2000-05-23 | 2000-05-23 | 2000-05-30 | 7.49 | 7.41 | 1.3 |  | 2 | 4 | 0 | 2 | 0 | 2 | 0 | 0 | 2 | 8 | 1.1 | 0.7 | 0 | 0
2000-05-29 | 2000-05-29 | 2000-06-05 | 7.5 | 7.49 | 1.1 |  | 2 | 4 | 0 | 3 | 0 | 3 | 0 | 2 | 2 | 12 | 1.1 | 0.7 | 0 | 0
2000-06-05 | 2000-06-05 | 2000-06-12 | 7.42 | 7.44 | 1 |  | 1 | 4 | 0 | 3 | 0 | 3 | 0 | 2 | 1 | 12 | 1.05 | 0.8 | 0 | 0
2000-06-12 | 2000-06-12 | 2000-06-19 | 7.53 | 7.39 | 1 |  | 2 | 3 | 0 | 2 | 0 | 2 | 0 | 1 | 2 | 8 | 0.95 | 0.7 | 0 | 0
2000-06-19 | 2000-06-19 | 2000-06-26 | 7.52 | 7.45 | 1 |  | 2 | 4 | 0 | 3 | 0 | 4 | 0 | 2 | 2 | 13 | 1.1 | 0.7 | 0 | 0
2000-06-26 | 2000-06-26 | 2000-07-03 | 7.5 | 7.56 | 1.2 |  | 3 | 7 | 0 | 5 | 0 | 6 | 0 | 3 | 3 | 21 | 1.05 | 0.7 | 0
2000-07-03 | 2000-07-03 | 2000-07-10 | 7.51 | 7.4 | 1.1 |  | 5 | 9 | 0 | 6 | 0 | 5 | 0 | 2 | 5 | 22 | 1.1 | 0.45 | 0 | 0
2000-07-10 | 2000-07-10 | 2000-07-17 | 7.52 | 7.48 | 1.5 |  | 7 | 11 | 0 | 6 | 0 | 6 | 0 | 2 | 7 | 25 | 1.15 | 0.45 | 0 | 0
2000-07-17 | 2000-07-17 | 2000-07-24 | 7.52 | 7.48 | 2.7 |  | 20 | 27 | 2 | 11 | 0 | 7 | 0 | 2 | 22 | 47 | 1.1 | 0.4 | 0 | 0
2000-07-24 | 2000-07-24 | 2000-07-31 | 7.27 | 7.3 | 2.2 |  | 23 | 31 | 2 | 10 | 0 | 5 | 0 | 1 | 25 | 47 | 0.95 | 0.4 | 0 | 0
2000-08-04 | 2000-08-04 | 2000-08-11 | 7.24 | 7.48 | 2.5 |  | 34 | 43 | 4 | 13 | 0 | 6 | 0 | 1 | 38 | 63 | 1.05 | 0.35 | 0 | 0.1
2000-08-08 | 2000-08-08 | 2000-08-15 | 7.37 | 7.38 | 2.5 |  | 37 | 35 | 4 | 4 | 0 | 0 | 0 | 0 | 41 | 39 | 1.05 | 0.15 | 0.1 | 0
2000-08-14 | 2000-08-14 | 2000-08-21 | 7.29 | 7.39 | 2.9 |  | 38 | 48 | 7 | 19 | 1 | 7 | 0 | 2 | 46 | 76 | 1.15 | 0.15 | 0 | 0
2000-08-21 | 2000-08-21 | 2000-08-28 | 7.42 | 7.44 | 1.9 |  | 24 | 31 | 4 | 12 | 0 | 5 | 0 | 1 | 28 | 49 | 1.15 | 0 | 0.05 | 0
2000-08-29 | 2000-08-29 | 2000-09-05 | 7.25 | 7.18 | 2.4 |  | 38 | 41 | 9 | 14 | 1 | 4 | 0 | 1 | 48 | 60 | 1.2 | 1.15 | 0.1 | 0
2000-09-05 | 2000-09-05 | 2000-09-12 | 7.32 | 7.23 | 2.7 |  | 34 | 42 | 9 | 17 | 0 | 5 | 0 | 1 | 43 | 65 | 1.15 | 0.05 | 0 | 0
2000-09-11 | 2000-09-11 | 2000-09-18 | 7.23 | 7.25 | 2.8 |  | 33 | 41 | 9 | 16 | 0 | 4 | 0 | 1 | 42 | 62 | 1.1 | 0.05 | 0 | 0
2000-09-18 | 2000-09-18 | 2000-09-25 | 7.21 | 7.25 | 2.9 |  | 33 | 41 | 11 | 18 | 1 | 5 | 0 | 1 | 45 | 65 | 1.1 | 0.15 | 0 | 0.15
2000-09-25 | 2000-09-25 | 2000-10-02 | 7.33 | 7.38 | 2.5 |  | 27 | 40 | 9 | 19 | 1 | 5 | 0 | 1 | 37 | 65 | 1.2 | 0.1 | 0 | 0
2000-10-02 | 2000-10-02 | 2000-10-10 | 7.52 | 7.15 | 2.9 |  | 31 | 37 | 11 | 17 | 1 | 4 | 0 | 1 | 43 | 59 | 0.8 | 0.05 | 0.1 | 0
2000-10-10 | 2000-10-10 | 2000-10-16 | 7.3 | 7.26 | 3.6 |  | 23 | 34 | 9 | 17 | 1 | 4 | 0 | 1 | 33 | 56 | 1.15 | 0.05 | 0 | 0
2000-10-16 | 2000-10-16 | 2000-10-23 | 7.35 | 7.48 | 3.6 |  | 24 | 37 | 10 | 20 | 1 | 5 | 0 | 1 | 35 | 63 | 0.95 | 0.05 | 0.1 | 0
2000-10-23 | 2000-10-23 | 2000-10-30 | 7.49 | 7.4 | 3.6 |  | 22 | 35 | 10 | 19 | 1 | 6 | 0 | 1 | 33 | 61 | 1.15 | 0.05 | 0.1 | 0
2000-10-31 | 2000-10-31 | 2000-11-06 | 7.31 | 7.31 | 3.6 |  | 19 | 30 | 10 | 18 | 1 | 5 | 0 | 1 | 30 | 54 | 1.2 | 0 | 0.1 | 0
2000-11-07 | 2000-11-07 | 2000-11-13 | 7.28 | 7.44 | 3.6 |  | 20 | 31 | 12 | 17 | 2 | 3 | 0 | 0 | 34 | 51 | 1.1 | 0.05 | 0.1 | 0
2000-11-13 | 2000-11-13 | 2000-11-20 | 7.4 | 7.36 | 3.9 |  | 17 | 30 | 8 | 17 | 1 | 3 | 0 | 0 | 26 | 50 | 1.15 | 0 | 0.1 | 0.1
2000-11-20 | 2000-11-20 | 2000-11-27 | 7.25 | 7.34 | 4.6 |  | 18 | 39 | 7 | 22 | 1 | 4 | 0 | 0 | 26 | 65 | 1.05 | 0 | 0.2 | 0
2000-11-27 | 2000-11-27 | 2000-12-04 | 7.28 | 7.4 | 4.8 |  | 17 | 40 | 9 | 23 | 2 | 5 | 0 | 0 | 28 | 68 | 1.05 | 0 | 0.2 | 0
2000-12-04 | 2000-12-04 | 2000-12-11 | 7.11 | 7.32 | 4.7 |  | 18 | 34 | 7 | 20 | 2 | 4 | 0 | 0 | 27 | 58 | 1.1 | 0 | 0.2 | 0
2000-12-11 | 2000-12-11 | 2000-12-18 | 7.37 | 7.35 | 5 |  | 19 | 45 | 8 | 24 | 2 | 4 | 0 | 0 | 29 | 73 | 1.05 | 0 | 0.2 | 0
2000-12-22 | 2000-12-22 | 2000-12-29 | 7.41 |  | 5.2 |  | 20 |  | 11 |  | 2 |  | 0 |  | 33 | 0 | 1 |  | 0.15
2000-12-27 | 2000-12-27 | 2001-01-03 | 7.46 | 7.51 |  |  | 22 | 52 | 12 | 28 | 2 | 5 | 0 | 0 | 36 | 85 | 1.1 | 0 | 0.3 | 0
2001-01-03 | 2001-01-03 | 2001-01-10 | 7.27 | 7.35 | 5.3 |  | 19 | 50 | 9 | 28 | 2 | 5 | 0 | 0 | 30 | 83 | 1.05 | 0 | 0.2 | 0
2001-01-08 | 2001-01-08 | 2001-01-15 | 7.46 | 7.41 | 5.5 |  | 22 | 44 | 12 | 26 | 2 | 5 | 0 | 0 | 36 | 75 | 1.15 | 0 | 0.35 | 0
2001-01-15 | 2001-01-15 | 2001-01-22 | 7.43 | 7.55 | 5.4 |  | 22 | 46 | 11 | 27 | 2 | 5 | 0 | 1 | 35 | 79 | 1.05 | 0 | 0.6 | 0.15
2001-01-22 | 2001-01-22 | 2001-01-29 | 7.38 | 7.34 | 5.4 |  | 22 | 55 | 12 | 30 | 2 | 6 | 0 | 0 | 36 | 91 | 1.1 | 0 | 0.6 | 0.1
2001-01-29 | 2001-01-29 | 2001-02-05 | 7.29 | 7.28 | 5.3 |  | 19 | 45 | 12 | 26 | 2 | 6 | 0 | 1 | 33 | 78 | 1.05 | 0 | 0.4 | 0
2001-02-05 | 2001-02-05 | 2001-02-12 | 7.25 | 7.12 | 5.4 |  | 19 | 48 | 11 | 28 | 2 | 6 | 0 | 1 | 32 | 83 | 1.05 | 0 | 0.45 | 0.15
2001-02-12 | 2001-02-12 | 2001-02-19 | 6.91 | 7.01 | 5.6 |  | 18 | 48 | 11 | 28 | 2 | 6 | 0 | 1 | 31 | 83 | 1.05 | 0 | 0.5 | 0.35
2001-02-19 | 2001-02-19 | 2001-02-26 | 7.24 | 7.25 | 5.5 |  | 19 | 54 | 10 | 26 | 2 | 4 | 0 | 0 | 31 | 84 | 1.05 | 0 | 0.4 | 0
2001-03-05 | 2001-03-05 | 2001-03-12 | 7.4 | 7.49 | 5.6 |  | 21 | 55 | 11 | 28 | 2 | 6 | 0 | 0 | 34 | 89 | 0.9 | 0 | 0.4 | 0.1
2001-03-12 | 2001-03-12 | 2001-03-19 | 7.1 | 7.23 | 5.6 |  | 22 | 45 | 12 | 28 | 3 | 6 | 0 | 0 | 37 | 79 | 1 | 0 | 0.5 | 0.1
2001-03-19 | 2001-03-19 | 2001-03-26 | 7.26 | 7.36 | 5.4 |  | 19 | 62 | 13 | 28 | 3 | 5 | 0 | 0 | 35 | 95 | 1.15 | 0 |  | 0.15
2001-03-26 | 2001-03-26 | 2001-04-02 | 7.28 | 7.27 | 5.2 |  | 21 | 54 | 10 | 26 | 2 | 5 | 0 | 0 | 33 | 85 | 1 | 0 | 0.45 | 0.1
2001-04-02 | 2001-04-02 | 2001-04-09 | 7.26 | 7.37 | 5.3 |  | 25 | 59 | 11 | 26 | 2 | 4 | 0 | 0 | 38 | 89 | 1.05 | 0 | 0.45 | 0.1
2001-04-10 | 2001-04-10 | 2001-04-17 | 7.32 | 7.25 | 4.4 |  | 18 | 50 | 11 | 23 | 2 | 4 | 0 | 0 | 31 | 77 | 0.95 | 0 | 0.25 | 0.15
2001-04-23 | 2001-04-23 | 2001-04-30 | 7.43 | 7.61 | 5 |  | 23 | 56 | 11 | 24 | 2 | 5 | 0 | 0 | 36 | 85 | 1.05 | 0 | 0.3 | 0.15
2001-04-30 | 2001-04-30 | 2001-05-07 | 7.25 | 7.37 | 3.3 |  | 16 | 42 | 6 | 14 | 1 | 2 | 0 | 0 | 23 | 58 | 1 | 0 | 0.3 | 0.1
2001-05-07 | 2001-05-07 | 2001-05-14 | 7.32 | 7.44 | 4.1 |  | 27 | 59 | 11 | 21 | 2 | 4 | 0 | 0 | 40 | 84 | 1.15 | 0 | 0.35 | 0.15
2001-05-14 | 2001-05-14 | 2001-05-22 | 7.32 | 7.53 | 4.3 |  | 28 | 59 | 13 | 21 | 3 | 4 | 0 | 0 | 44 | 84 | 1.05 | 0.05 | 0.3 | 0.1
2001-05-22 | 2001-05-29 | 2001-05-29 | 7.3 | 7.35 | 4.1 |  | 25 | 59 | 12 | 21 | 2 | 3 | 0 | 0 | 39 | 83 | 1.1 | 0 | 0.35 | 0.2
2001-05-28 | 2001-05-28 | 2001-06-04 | 7.27 | 7.32 | 4.5 |  | 27 | 57 | 13 | 21 | 2 | 0 | 0 | 0 | 42 | 78 | 1.05 | 0 | 0.3 | 0.15
2001-06-04 | 2001-06-04 | 2001-06-11 | 7.58 | 7.59 | 1.1 |  | 0 | 3 | 0 | 2 | 0 | 2 | 0 | 1 | 0 | 8 | 1 | 0.45 | 0 | 0
2001-06-11 | 2001-06-11 | 2001-06-18 | 7.34 | 7.5 | 0.9 |  | 0 | 3 | 0 | 2 | 0 | 3 | 0 | 9 | 0 | 17 | 0.95 | 0.2 | 0 | 0
2001-06-18 | 2001-06-18 | 2001-06-25 | 7.41 | 7.48 | 1 |  | 1 | 4 | 0 | 3 | 0 | 4 | 0 | 2 | 1 | 13 | 1 | 0.1 | 0 | 0
2001-06-25 | 2001-06-25 | 2001-07-02 | 7.45 | 7.46 | 1.2 |  | 1 | 4 | 0 | 4 | 0 | 5 | 0 | 3 | 1 | 16 | 0.95 | 0.2 | 0 | 0
2001-07-02 | 2001-07-02 | 2001-07-09 | 7.64 | 7.52 | 1.4 |  | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 0.95 | 0.1 | 0 | 0
2001-07-09 | 2001-07-09 | 2001-07-16 | 7.36 | 7.49 | 1.6 |  | 5 | 7 | 0 | 4 | 0 | 4 | 0 | 2 | 5 | 17 | 1.1 | 0.35 | 0 | 0.1
2001-07-16 | 2001-07-16 | 2001-07-23 | 7.39 | 7.43 | 1.6 |  | 7 | 10 | 0 | 4 | 0 | 5 | 0 | 3 | 7 | 22 | 1 | 0.35 | 0.1 | 0.1
2001-07-23 | 2001-07-23 | 2001-07-30 | 7.39 | 7.36 | 2.1 |  | 13 | 20 | 1 | 9 | 0 | 7 | 0 | 2 | 14 | 38 | 1 | 0.2 | 0.1 | 0.1
2001-07-31 | 2001-07-31 | 2001-08-07 | 7.43 | 7.24 | 2 |  | 19 | 22 | 1 | 1 | 1 | 1 | 0 | 0 | 21 | 24 | 1.05 | 0.2 | 0.1 | 0.1
2001-08-07 | 2001-08-07 | 2001-08-13 | 7.33 | 7.43 | 2.4 |  | 34 | 45 | 3 | 11 | 1 | 6 | 0 | 1 | 38 | 63 | 1 | 0.2 | 0.1 | 0.15 | Only 6 days!
2001-08-13 | 2001-08-13 | 2001-08-20 | 7.26 | 7.21 | 2.2 |  | 40 | 53 | 4 | 12 | 0 | 5 | 0 | 1 | 44 | 71 | 1.1 | 0.15 | 0.1 | 0.1
2001-08-20 | 2001-08-20 | 2001-08-27 | 7.19 | 7.18 | 2.4 |  | 43 | 57 | 6 | 14 | 0 | 5 | 0 | 0 | 49 | 76 | 1.35 | 0.15 | 0.1 | 0.1
2001-08-28 | 2001-08-28 | 2001-09-04 | 7.17 | 7.11 | 2.4 |  | 43 | 53 | 9 | 15 | 1 | 4 | 0 | 0 | 53 | 72 | 1.1 | 0.2 | 0.1 | 0.1
2001-09-04 | 2001-09-04 | 2001-09-11 | 7.14 | 7.26 | 2.5 |  | 38 | 41 | 9 | 11 | 1 | 2 | 0 | 0 | 48 | 54 | 1 | 0.15 | 0.1 | 0.1
2001-09-10 | 2001-09-10 | 2001-09-17 | 7.25 | 7.23 | 2.6 |  | 35 | 50 | 9 | 17 | 1 | 4 | 1 | 1 | 46 | 72 | 1.1 | 0.2 | 0.1 | 0.1
2001-09-17 | 2001-09-17 | 2001-09-24 | 7.19 | 7.26 | 3.1 |  | 37 | 45 | 10 | 15 | 1 | 4 | 0 | 0 | 48 | 64 | 1 | 0.15 | 0.15 | 0.1
2001-09-24 | 2001-09-24 | 2001-10-01 | 7.25 | 7.34 | 3.2 |  | 34 | 47 | 10 | 17 | 1 | 4 | 0 | 1 | 45 | 69 | 1.15 | 0.15 | 0.1 | 0.1
2001-10-02 | 2001-10-02 | 2001-10-09 | 7.33 | 7.42 | 3.2 |  | 34 | 56 | 11 | 21 | 1 | 6 | 0 | 0 | 46 | 83 | 1.05 | 0.1 | 0.15 | 0.1
2001-10-09 | 2001-10-09 | 2001-10-17 | 7.26 | 7.23 | 3.2 |  | 32 | 52 | 10 | 20 | 1 | 5 | 0 | 0 | 43 | 77 | 1 | 0.05 | 0.15 | 0.1 | 8 days
2001-10-15 | 2001-10-15 | 2001-10-22 | 7.3 | 7.04 | 2.8 |  | 29 | 49 | 9 | 18 | 1 | 4 | 0 | 0 | 39 | 71 | 1.1 | 0.1 | 0.1 | 0.1
2001-10-22 | 2001-10-22 | 2001-10-29 | 7.31 | 7.43 | 2.7 |  | 26 | 34 | 9 | 15 | 1 | 5 | 0 | 1 | 36 | 55 | 1.1 | 0.15 | 0.15 | 0.15
2001-10-29 | 2001-10-29 | 2001-11-05 | 7.18 | 7.33 | 2.9 |  | 25 | 43 | 9 | 17 | 1 | 4 | 0 | 0 | 35 | 64 | 1.1 | 0.05 | 0.1 | 0.15
2001-11-05 | 2001-11-05 | 2001-11-12 | 7.2 | 7.35 | 3.2 |  | 23 | 48 | 8 | 19 | 1 | 5 | 0 | 1 | 32 | 73 | 1.05 | 0.1 | 0.15 | 0.1
2001-11-12 | 2001-11-12 | 2001-11-19 | 7.08 | 7.32 | 3.2 |  | 22 | 44 | 8 | 18 | 1 | 4 | 0 | 0 | 31 | 66 | 1.15 | 0.05 | 0.15 | 0.1
2001-11-19 | 2001-11-19 | 2001-11-26 | 7.33 | 7.3 | 3.6 |  | 21 | 44 | 8 | 18 | 1 | 4 | 0 | 0 | 30 | 66 | 1.05 | 0.05 | 0.15 | 0.1
2001-11-26 | 2001-11-26 | 2001-12-03 | 7.43 | 7.58 | 4.4 |  | 18 | 76 | 6 | 22 | 1 | 4 | 0 | 0 | 25 | 102 | 1.15 | 0 | 0.25 | 0.15
2001-12-04 | 2001-12-04 | 2001-12-11 | 7.14 | 7.31 | 4.1 |  | 19 | 53 | 6 | 19 | 2 | 4 | 0 | 0 | 27 | 76 | 1.2 | 0 | 0.3 | 0.1
2001-12-10 | 2001-12-10 | 2001-12-17 | 7.33 | 7.25 | 4.3 |  | 19 | 62 | 7 | 21 | 2 | 4 | 0 | 0 | 28 | 87 | 1.2 | 0 | 0.35 | 0.15
2001-12-17 | 2001-12-17 | 2001-12-24 | 7.3 | 7.36 | 4.4 |  | 20 | 55 | 8 | 21 | 2 | 4 | 0 | 0 | 30 | 80 | 1.15 | 0 | 0.35 | 0.15
2001-12-24 | 2001-12-24 | 2001-12-31 | 7.3 | 6.94 |  |  | 19 | 59 | 7 | 21 | 2 | 4 | 0 | 0 | 28 | 84 | 1.15 | 0 | 0.35 | 0.2
|  | Average: | 7.2101 | 7.2369 | 3.8343 | #DIV/0! | 22.8201 | 42.0507 | 8.3669 | 19.5 | 1.5108 | 5.2391 | 0.0071942 | 0.66667 | 32.705 | 66.9712 | 1.0871 | 0.13696 | 0.16957 | 0.055109
|  | % Difference: |  | 0.3702% |  | #DIV/0! |  | 45.73% |  | 57.09% |  | 71.16% |  | 98.92% |  | 51.17% |  | 87.4% |  | 67.5%
|  | Total Tests for 2001: | 49 | 49 | 49 |  | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 48 | 49 | 832

## preGAC THMFP
preGAC - SDSTHMC
| Date |  |  | pH |  | DOC (mg/L) |  | Trihalomethanes (µg/L) | [9 empty] | Chlorine (mg/L)
| Collected | Initial (I) Analyzed | Final (F) Analyzed | I pH | F pH | I DOC | F DOC | I CHCl3 | F CHCl3 | I CHCl2Br | F CHCl2Br | I CHBr2Cl | F CHBr2Cl | I CHBr3 | F CHBr3 | I Total | F Total | I Free | F Free | I Combined | F Combined
| 1999-06-21 | 1999-06-21 | 1999-06-28 | 6.96 | 6.91 | 5 |  | 55 | 58 | 17 | 18 | 2 | 2 | 0 | 0 | 74 | 78 | 0.15 | 0 | 0.15 | 0
| 36339 | 36339 | 36346 | 6.88 | 7.1 | 4.9 |  | 43 | 66 | 14 | 23 | 2 | 3 | 0 | 0 | 59 | 92 | 0.2 | 0 | 0.25 | 0
| 36346 | 36346 | 36353 | 7.01 | 6.96 | 5 |  | 48 | 64 | 17 | 17 | 2 | 2 | 0 | 0 | 67 | 83 | 0.1 | 0 | 0.25 | 0
| 36353 | 36353 | 36360 | 6.92 | 6.79 | 5.1 |  | 51 | 64 | 18 | 21 | 2 | 3 | 0 | 0 | 71 | 88 | 0.15 | 0 | 0.2 | 0
| 36360 | 36360 | 36367 | 6.94 | 6.88 | 5 |  | 52 | 70 | 19 | 25 | 2 | 2 | 0 | 0 | 73 | 97 | 0.15 | 0 | 0.25 | 0
| 36367 | 36367 | 36375 | 6.92 | 6.79 | 5.9 |  | 58 | 67 | 21 | 23 | 2 | 2 | 0 | 0 | 81 | 92 | 0.05 | 0 | 0.3 | 0
| 36375 | 36375 | 36381 | 6.78 | 6.5 | 5.4 |  | 47 | 70 | 19 | 27 | 2 | 3 | 0 | 0 | 68 | 100 | 0.2 | 0 | 0.3 | 0
| 36381 | 36381 | 36388 | 6.71 | 6.6 | 5.8 |  | 54 | 76 | 22 | 30 | 2 | 3 | 0 | 0 | 78 | 109 | 0.05 | 0 | 0.4 | 0
| 36388 | 36388 | 36395 | 6.62 | 6.79 | 5.7 |  | 63 | 83 | 26 | 31 | 3 | 4 | 0 | 0 | 92 | 118 | 0.15 | 0 | 0.35 | 0
| 36395 | 36395 | 36402 | 6.56 | 6.6 | 5.2 |  | 51 | 68 | 24 | 32 | 3 | 4 | 0 | 0 | 78 | 104 | 0.15 | 0 | 0.35 | 0
| 36430 | 36430 | 36437 | 6.89 | 6.77 | 5.5 |  | 30 | 44 | 18 | 23 | 3 | 0 | 0 | 0 | 51 | 67 | 0.25 | 0 | 0.3 | 0
| 36437 | 36437 | 36445 | 6.79 | 6.96 | 5.5 |  | 22 | 33 | 13 | 18 | 2 | 3 | 0 | 0 | 37 | 54 | 0.2 | 0 | 0.3 | 0
| 36445 | 36445 | 36452 | 6.8 | 6.66 | 6 |  | 18 | 26 | 13 | 12 | 2 | 2 | 0 | 0 | 33 | 40 | 0.1 | 0 | 0.2 | 0
| 36452 | 36452 | 36459 | 6.8 | 6.89 | 5.8 |  | 15 | 28 | 10 | 21 | 2 | 4 | 0 | 0 | 27 | 53 | 0.2 | 0 | 0.05 | 0
| 36458 | 36458 | 36465 | 6.86 | 6.93 | 5.7 |  | 17 | 29 | 12 | 18 | 2 | 4 | 0 | 0 | 31 | 51 | 0.25 | 0 | 0.25 | 0
| 36465 | 36465 | 36472 | 6.81 | 6.77 | 5.9 |  | 18 | 28 | 13 | 20 | 2 | 4 | 0 | 0 | 33 | 52 | 0.05 | 0 | 0.25 | 0
| 36472 | 36472 | 36479 | 6.75 | 6.97 | 5.7 |  | 16 | 27 | 11 | 21 | 3 | 4 | 0 | 0 | 30 | 52 | 0.15 | 0 | 0.25 | 0
| 36696 | 36696 | 36703 | 7.31 | 7.23 | 4.6 |  | 24 | 30 | 13 | 15 | 2 | 2 | 0 | 0 | 39 | 47 | 0.15 | 0 | N/A | 0
| 36703 | 36703 | 36710 | 7.1 | 7.22 | 4.5 |  | 34 | 44 | 15 | 19 | 2 | 3 | 0 | 0 | 51 | 66 | 0.15 | 0 | 0.2 | 0
| 36710 | 36710 | 36717 | 7 | 6.92 | 4.4 |  | 36 | 45 | 15 | 18 | 2 | 2 | 0 | 0 | 53 | 65 | 0.1 | 0 | 0.05 | 0
| 36717 | 36717 | 36724 | 7.05 | 7.04 | 4.5 |  | 42 | 50 | 17 | 19 | 2 | 2 | 0 | 0 | 61 | 71 | 0.1 | 0 | 0.1 | 0
| 36724 | 36724 | 36731 | 7 | 7.05 | 5.2 |  | 45 | 60 | 16 | 21 | 2 | 2 | 0 | 0 | 63 | 83 | 0.1 | 0 | 0.2 | 0
| 36731 | 36731 | 36738 | 6.96 | 7.02 | 4.7 |  | 38 | 52 | 15 | 16 | 2 | 2 | 0 | 0 | 55 | 70 | 0.2 | 0 | 0.15 | 0
| 36742 | 36742 | 36749 | 6.96 | 7.2 | 4.9 |  | 35 | 48 | 15 | 16 | 2 | 2 | 0 | 0 | 52 | 66 | 0.1 | 0 | 0.25 | 0
| 36746 | 36746 | 36753 | 7 | 7.07 | 4.7 |  | 40 | 47 | 15 | 14 | 2 | 2 | 0 | 0 | 57 | 63 | 0.1 | 0 | 0.2 | 0
| 36752 | 36752 | 36759 | 7.01 | 7.08 | 5.3 |  | 43 | 55 | 16 | 20 | 2 | 2 | 0 | 0 | 61 | 77 | 0.05 | 0 | 0.25 | 0
| 36759 | 36759 | 36766 | 7.13 | 7.13 | 4.7 |  | 37 | 47 | 15 | 14 | 2 | 2 | 0 | 0 | 54 | 63 | 0.25 | 0 | -- | 0
| 36767 | 36767 | 36774 | 6.95 | 6.94 | 4.6 |  | 34 | 45 | 14 | 18 | 2 | 2 | 0 | 0 | 50 | 65 | 0.2 | 0 | 0.25 | 0
| 36774 | 36774 | 36781 | 6.94 | 6.94 | 4.5 |  | 27 | 39 | 11 | 17 | 1 | 2 | 0 | 0 | 39 | 58 | 0.2 | 0 | 0.25 | 0
| 36780 | 36780 | 36787 | 7.02 | 7.06 | 4.6 |  | 26 | 40 | 11 | 17 | 1 | 2 |  | 0 | 38 | 59 | 0.25 | 0 | 0.3 | 0
| 36787 | 36787 | 36794 | 7.01 | 6.98 | 4.3 |  | 27 | 33 | 12 | 15 | 1 | 2 | 0 | 0 | 40 | 50 | 0.2 | 0 | 0.25 | 0
| 36794 | 36794 | 36801 | 6.92 | 7.07 | 4.2 |  | 24 | 31 | 10 | 12 | 2 | 2 | 0 | 0 | 36 | 45 | 0.15 | 0 | 0.2 | 0
| 36801 | 36801 | 36809 | 7.27 | 7.09 | 4.2 |  | 23 | 29 | 11 | 14 | 1 | 2 | 0 | 0 | 35 | 45 | 0 | 0 | 0.15 | 0
| 36809 | 36809 | 36815 | 7.08 | 7.03 | 4.8 |  | 17 | 24 | 8 | 13 | 1 | 2 | 0 | 0 | 26 | 39 | 0.2 | 0 | 0.2 | 0
| 36815 | 36815 | 36822 | 7.13 | 7.34 | 4.6 |  | 17 | 26 | 8 | 13 | 1 | 2 | 0 | 0 | 26 | 41 | 0.15 | 0 | 0.25 | 0
| 36822 | 36822 | 36829 | 7.17 | 7.15 | 4.7 |  | 21 | 32 | 9 | 16 | 2 | 3 | 0 | 0 | 32 | 51 | 15 | 0 | 0.25 | 0
| 36830 | 36830 | 36836 | 7.14 | 7.13 | 4.6 |  | 16 | 27 | 7 | 15 | 1 | 3 | 0 | 0 | 24 | 45 | 0.35 | 0 | 0.25 | 0
| 36837 | 36837 | 36843 | 7.06 | 7.32 | 4.4 |  | 17 | 23 | 10 | 13 | 2 | 2 | 0 | 0 | 29 | 38 | 0.15 | 0 | 0 | 0
| 36843 | 36843 | 36850 | 7.26 | 7.13 | 4.5 |  | 12 | 15 | 6 | 9 | 1 | 2 | 0 | 0 | 19 | 26 | 0.2 | 0 | 0.2 | 0
| 37046 | 37046 | 37053 | 7.26 | 7.31 | 4.3 |  | 25 | 34 | 12 | 17 | 3 | 4 | 1 | 1 | 41 | 56 | 0.25 | 0 | 0.3 | 0.1
| 37053 | 37053 | 37060 | 7.22 | 7.42 | 4.7 |  | 20 | 28 | 10 | 14 | 2 | 4 | 0 | 0 | 32 | 46 | 0.15 | 0 | 0.25 | 0
| 37060 | 37060 | 37067 | 7.22 | 7.35 | 4.5 |  | 27 | 34 | 13 | 15 | 3 | 4 | 0 | 0 | 43 | 53 | 0.15 | 0 | 0.35 | 0
| 37067 | 37067 | 37074 | 7.13 | 7.11 | 4.7 |  | 29 | 35 | 13 | 16 | 3 | 4 | 1 | 0 | 46 | 55 | 0.1 | 0 | 0.3 | 0
| 37074 | 37074 | 37081 | 7.13 | 7.28 | 4.8 |  | 38 | 43 | 17 | 16 | 4 | 4 | 0 | 0 | 59 | 63 | 0.15 | 0 | 0.35 | 0
| 37081 | 37081 | 37088 | 7.12 | 7.44 | 4.6 |  | 29 | 31 | 13 | 14 | 3 | 3 | 0 | 0 | 45 | 48 | 0.15 | 0 | 0.25 | 0
| 37088 | 37088 | 37095 | 7.12 | 7.32 | 4.4 |  | 34 | 42 | 14 | 16 | 3 | 4 | 0 | 0 | 51 | 62 | 0.1 | 0 | 0.3 | 0
| 37095 | 37095 | 37102 | 7.08 | 7.15 | 4.8 |  | 40 | 52 | 15 | 17 | 3 | 3 | 0 | 0 | 58 | 72 | 0.05 | 0 | 0.4 | 0.1
| 37103 | 37103 | 37110 | 7.23 | 6.94 | 4.3 |  | 39 | 47 | 14 | 14 | 3 | 3 | 0 | 0 | 56 | 64 | 0.15 | 0 | 0.45 | 0.1
| 37110 | 37110 | 37116 | 7.07 | 7.2 | 4.6 |  | 40 | 60 | 14 | 19 | 2 | 3 | 0 | 0 | 56 | 82 | 0.45 | 0 | 0.3 | 0.1 | Only 6 days!
| 37116 | 37116 | 37123 | 7.13 | 7.07 | 4 |  | 36 | 54 | 13 | 16 | 2 | 3 | 0 | 0 | 51 | 73 | 0.55 | 0 | 0.45 | 0
| 37123 | 37123 | 37130 | 7.01 | 7.03 | 4.4 |  | 40 | 58 | 13 | 17 | 2 | 3 | 0 | 0 | 55 | 78 | 0.7 | 0 | 0.5 | 0.1
| 37131 | 37131 | 37138 | 6.96 | 6.94 | 4.3 |  | 33 | 61 | 12 | 17 | 2 | 3 | 0 | 0 | 47 | 81 | 0.6 | 0 | 0.45 | 0.15
| 37138 | 37138 | 37145 | 6.92 | 7.01 | 4 |  | 35 | 51 | 11 | 15 | 2 | 2 | 0 | 0 | 48 | 68 | 0.4 | 0 | 0.45 | 0.1
| 37144 | 37144 | 37151 | 6.95 | 6.96 | 4.3 |  | 29 | 64 | 9 | 18 | 2 | 3 | 0 | 0 | 40 | 85 | 0.75 | 0 | 0.45 | 0.2
2001-09-17 | 37151 | 37151 | 37158 | 6.97 | 7.06 | 5 |  | 31 | 45 | 10 | 14 | 2 | 2 | 0 | 0 | 43 | 61 | 0.5 | 0 | 0.45 | 0.1
| 37158 | 37158 | 37165 | 6.97 | 7.07 | 4.9 |  | 30 | 54 | 10 | 16 | 2 | 2 | 0 | 0 | 42 | 72 | 0.55 | 0 | 0.45 | 0.15
| 37166 | 37166 | 37173 | 7.01 | 7.13 | 5.1 |  | 31 | 48 | 11 | 15 | 2 | 2 | 0 | 0 | 44 | 65 | 0.4 | 0 | 0.4 | 0.1
| 37173 | 37173 | 37181 | 7.03 | 6.99 | 4.8 |  | 29 | 42 | 10 | 13 | 2 | 2 | 0 | 0 | 41 | 57 | 0.35 | 0 | 0.35 | 0.1 | 8 days
| 37179 | 37179 | 37186 | 7.03 | 6.78 | 4.1 |  | 26 | 46 | 9 | 15 | 2 | 2 | 0 | 0 | 37 | 63 | 0.9 | 0 | 0.4 | 0.1
| 37186 | 37186 | 37193 | 6.92 | 7.06 | 4.3 |  | 25 | 48 | 9 | 16 | 2 | 3 | 0 | 0 | 36 | 67 | 0.75 | 0 | 0.45 | 0.1
| 37193 | 37193 | 37200 | 6.88 | 6.99 | 4 |  | 16 | 35 | 6 | 14 | 1 | 3 | 0 | 0 | 23 | 52 | 0.45 | 0 | 0.3 | 0.1
| 37200 | 37200 | 37207 | 6.94 | 7 | 4.2 |  | 20 | 38 | 8 | 15 | 2 | 3 | 0 | 0 | 30 | 56 | 0.5 | 0 | 0.25 | 0
| 37207 | 37207 | 37214 | 6.91 | 7.18 | 3.9 |  | 14 | 33 | 5 | 14 | 1 | 3 | 0 | 0 | 20 | 50 | 0.4 | 0 | 0.2 | 0
| 37214 | 37214 | 37221 | 7.19 | 7.14 | 4.2 |  | 16 | 27 | 6 | 12 | 1 | 3 | 0 | 0 | 23 | 42 | 0.4 | 0 | 0.3 | 0.1
[16 empty] | 0 | 0
[16 empty] | 0 | 0
[16 empty] | 0 | 0
[16 empty] | 0 | 0
[16 empty] | 0 | 0
[16 empty] | 0 | 0
[16 empty] | 0 | 0
[16 empty] | 0 | 0
[16 empty] | 0 | 0
[16 empty] | 0 | 0
[16 empty] | 0 | 0
[16 empty] | 0 | 0
[16 empty] | 0 | 0
[16 empty] | 0 | 0
[16 empty] | 0 | 0
[16 empty] | 0 | 0
[16 empty] | 0 | 0
[16 empty] | 0 | 0
[16 empty] | 0 | 0
[16 empty] | 0 | 0
[16 empty] | 0 | 0
[16 empty] | 0 | 0
[16 empty] | 0 | 0
[16 empty] | 0 | 0
|  |  | Average: | 6.998 | 7.0303 | 4.7781 | #DIV/0! | 31.6406 | 44.5781 | 13.0156 | 17.3281 | 2.0312 | 2.6719 | 0.031746 | 0.015625 | 33.9773 | 46.9773 | 0.48125 | 0 | 0.28145 | 0.028125
|  |  | % Difference: |  | 0.0046006 |  | #DIV/0! |  | 0.29022 |  | 0.24887 |  | 0.23977 |  | 0.50781 |  | 0.27673 |  | 1 |  | 0.90007
|  |  | Total Tests for 2001: | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 425

## Month Avg
2001 - BUFFALO POUND WATER QUALITY DATA
RAW LAKE WATER
page 1
| Parameters | Units | JAN Avg | FEB Avg | MAR Avg | APR Avg | MAY Avg | JUN Avg | JUL Avg | AUG Avg | SEP Avg | OCT Avg | NOV Avg | DEC Avg | YEAR AVG | YEAR MIN | YEAR MAX | Number of Tests Done
PHYSICAL
| Colour (Apparent) | Pt/Co | 15 | 15 | 16.25 | 32.5 | 40 | 35 | 48 | 50 | 55 | 51 | 38.75 | 15 | 35.3061 | 10 | 80 | 49
| Conductivity | µS/cm | 710 | 728 | 740.75 | 682.25 | 583.75 | 591.5 | 561.4 | 521.25 | 523.75 | 537.2 | 550.25 | 595 | 607.8776 | 509 | 749 | 49
| Bench Diss. Oxygen | mg/L | 8.36 | 6.4333 | 4.9 | 8.76 | 9.225 | 8.975 | 7.2 | 7.15 | 8.675 | 10.74 | 12.05 | 10.9 | 8.6686 | 3.7 | 12.4 | 50
| Bench Diss. Oxygen | % | 62.2664 | 48.3568 | 37.2832 | 71.4498 | 88.2528 | 94.1308 | 80.9669 | 80.8788 | 87.389 | 90.8023 | 88.4345 | 78.7885 | 76.3358 | 28.2012 | 100.8869 | 50
| ON-LINE Diss. Oxygen | % | 76.5 | 49 | 41.75 | 80.3 | 88 | 92.425 | 87.68 | 78.2 | 89.175 | 98.02 | 92.7 | 87.7333 | 81.1265 | 27 | 111.4 | 48
| Odour | T.O.N. | 13.5 | 14 | 19.6667 | 135 | 88.75 | 190 | 134.2 | 113 | 101.5 | 43.8 | 21.25 | 24.3333 | 81.6383 | 10 | 325 | 47
| Particles | per ml | 10159 | 13878 | 26731.5333 | 47697 | 56735.665 | 50015.675 | 54759 | 42749.25 | 39453.5 | 47862.75 | 40132.6667 | 14870.3333 | 38930.9293 | 8839 | 75906 | 43
| pH | pH units | 7.816 | 7.69 | 7.5625 | 7.754 | 8.2525 | 8.37 | 8.312 | 8.5125 | 8.3875 | 8.434 | 8.1725 | 7.9975 | 8.1112 | 7.49 | 8.61 | 50
| SST | mg/L | 2.3333 | 2.35 | 2.6667 | 8 | 10.5 | 14.5 | 14.56 | 13.05 | 14.65 | 22.12 | 10.9 | 4.0667 | 11.2205 | 1.9 | 45.6 | 44
| SSV | mg/L | 1.0667 | 0.9 | 1.4667 | 4.4667 | 3.4 | 5.95 | 5.78 | 8.35 | 10.65 | 11.72 | 2.45 | 2.0667 | 5.4477 | 0.7 | 20.8 | 44
| SSF | mg/L | 1.2667 | 1.45 | 1.2 | 3.5333 | 7.1 | 8.55 | 8.06 | 4.7 | 4 | 10.4 | 8.45 | 2 | 5.6909 | 0.8 | 24.8 | 44
| Temperature | ° C | 3.08 | 3.4 | 3.825 | 6.36 | 13.3 | 17.5 | 21.1 | 21.375 | 15.675 | 8.08 | 2.55 | 1.975 | 9.9627 | 0.5 | 23.4 | 50
| Turbidity | NTU | 2.132 | 2.15 | 2.0325 | 4.762 | 8.3475 | 12.5 | 10.808 | 11.2675 | 8.8375 | 9.776 | 9.1725 | 3.275 | 7.168 | 1.69 | 19.2 | 50
| TDS | mg/L(calc) | 569.7675 | 581.015 | 595.9275 | 551.876 | 464.51 | 471.875 | 434.685 | 408.9275 | 412.6175 | 421.548 | 435.14 | 471.16 | 481.2006 | 405.95 | 601.25
| Langelier Index (RTW) | pH units (calc) | 0.13253 | 0.0579 | -0.015425 | 0.16029 | 0.64175 | 0.82288 | 0.70223 | 0.88619 | 0.68019 | 0.66057 | 0.3469 | 0.24595 | 0.4627 | -0.0855 | 0.97961
MAJOR CONSTITUENTS
| Alkalinity(p) | mg/L CaCO3 | <1 | <1 | <1 | <1 | <1 | 2 | 2.2 | 3.75 | 2.75 | 4 | <1 | <1 | 1.3 | <1 | 7 | 50
| Alkalinity(total) | mg/L CaCO3 | 203.6 | 206.3333 | 215 | 200.6 | 170.75 | 170 | 151.2 | 144 | 146 | 155.2 | 161.75 | 175.6667 | 174.58 | 138 | 218 | 50
| Bicarbonate | mg/L | 248.2 | 251.6667 | 262 | 244.8 | 208 | 202.25 | 178.8 | 166.25 | 171.25 | 178.6 | 197.25 | 213.6667 | 209.52 | 156 | 266 | 50
| Carbonate | mg/L | <1 | <1 | <1 | <1 | <1 | 2.25 | 2.6 | 4.5 | 3.25 | 4.8 | <1 | <1 | 1.54 | <1 | 8 | 50
| Calcium | mg/L | 61.5 | 63 | 66 | 61.4 | 51.5 | 52 | 47.8 | 43.5 | 43.25 | 46.2 | 48.75 | 53 | 52.6667 | 42 | 66 | 48
| Magnesium | mg/L | 26.5 | 27 | 27 | 25.6 | 20.5 | 20.5 | 18.8 | 18.75 | 19.25 | 19.6 | 19.5 | 22 | 21.8333 | 17 | 28 | 48
| Hardness (total) | mg/L CaCO3 | 263.5 | 269 | 276.25 | 258.6 | 214.5 | 214.25 | 198.4 | 185.5 | 187.75 | 196.2 | 202.75 | 223 | 221.8958 | 185 | 280 | 48
| Sodium | mg/L | 53.75 | 54 | 54.5 | 51.2 | 43.5 | 45.75 | 43.75 | 40.5 | 39.5 | 38.6 | 38.25 | 41 | 45.0638 | 37 | 56 | 47
| Potassium | mg/L | 6.425 | 7.1 | 5.55 | 5.26 | 4.7 | 5 | 4.9 | 4.55 | 4.325 | 4.18 | 4 | 4.2 | 4.9319 | 4 | 7.8 | 47
| Sulphate | mg/L | 151.25 | 154.5 | 156.5 | 141.8 | 118.25 | 124.5 | 118.5 | 108.75 | 109 | 107 | 106.25 | 114.6667 | 124.8723 | 105 | 158 | 47
| Chloride | mg/L | 14.4 | 14.75 | 15.05 | 13.84 | 11.75 | 12.5 | 12.025 | 11.075 | 11.175 | 11.08 | 10.975 | 11.7667 | 12.4511 | 10.8 | 15.2 | 47
TRACE CONSTITUENTS
| Aluminum (dissolved 0.45µ) | ugL | 25.6 | 12 | <6 | <6 | 8.75 | 21.75 | 20.25 | 7.5 | 20.5 | 8.4 | 9 | 7 | 12.1702 | <6 | 59 | 47
| Aluminum (total) | ug/L | 107.4 | 106 | 81.75 | 124.5 | 441.5 | 311.875 | 425.25 | 212.25 | 212.25 | 441 | 496.75 | 142 | 268.1809 | 62 | 1020 | 47
| Aluminum (particulate) | µg/L (Calc) | 81.8 | 94 | 80.25 | 124.5 | 432.75 | 290.125 | 405 | 204.75 | 191.75 | 432.6 | 487.75 | 135 | 256.0106 | 62 | 1010 | 47
| Ammonia N | mg/L N | 0.06 | 0.08 | <0.04 | <0.04 | 0.055 | 0.0625 | 0.066 | 0.0525 | 0.075 | 0.08 | 0.075 | 0.046667 | 0.057674 | <0.04 | 0.12 | 43
| BOD (5-day) | mg/L | 2.2 | 1.8 | 2.3667 | 4.3333 | 2.1667 | 2.3 | 4.125 | 2.55 | 2.275 | 3.78 | 2.75 | 2.75 | 2.8405 | 0.5 | 7.2 | 42
| Bromide | mg/L | <0.06 | <0.06 | <0.06 | <0.06 | <0.06 | <0.06 | <0.06 | <0.06 | <0.06 | <0.06 | <0.06 | <0.06 | <0.06 | <0.06 | <0.06 | 47
| Chlorophyll a | µg/L | 7 | 6 | 13.6667 | 24.75 | 12.75 | 34.5 | 40.6 | 50.25 | 46.5 | 28.4 | 9.25 | 12.3333 | 25.5435 | 2 | 60 | 46
| Fluoride | mg/L | 0.2 | 0.20333 | 0.2075 | 0.194 | 0.185 | 0.1975 | 0.208 | 0.2075 | 0.22 | 0.216 | 0.2 | 0.20667 | 0.2038 | 0.17 | 0.22 | 50
| Iron (dissolved) | mg/L | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | 42
| Iron (total) | mg/L | 0.05 | 0.08 | 0.056667 | 0.0975 | 0.2275 | 0.175 | 0.204 | 0.1225 | 0.1 | 0.232 | 0.17333 | 0.06 | 0.14643 | 0.03 | 0.48 | 42
| Manganese (dissolved) | mg/L | 0.01 | 0.015 | 0.07 | 0.2075 | <0.01 | <0.01 | <0.01 | <0.01 | <0.01 | 0.006 | <0.01 | 0.0066667 | 0.027619 | <0.01 | 0.29 | 42
| Manganese(total) | mg/L | 0.04 | 0.065 | 0.14 | 0.31 | 0.055 | 0.0575 | 0.096 | 0.0625 | 0.04 | 0.036 | 0.02 | 0.016667 | 0.082381 | 0.01 | 0.42 | 42
| Nitrate | mg/L | 0.055 | 0.135 | 0.2125 | <0.06 | <0.06 | <0.06 | <0.06 | <0.06 | <0.06 | <0.06 | <0.06 | <0.06 | <0.06 | <0.06 | 0.25 | 47
| Organic N | mg/L | 0.545 | 0.55 | 0.48667 | 0.7275 | 0.6425 | 0.905 | 1.02 | 1.0025 | 1.2875 | 1.16 | 0.5775 | 0.62667 | 0.84767 | 0.35 | 1.6 | 43
| Raw TOC | mg/L C (UV) | 8.84 | 8.5333 | 8.1 | 9 | 7.975 | 9.075 | 9.4333 | 10.0333 | 11.3 | 10.18 | 7.5 | 7.3667 | 9.042 | 7 | 12
| Raw DOC (GF diss) | mg/L C (UV) | 8.3 | 8.025 | 7.725 | 7.5 | 6.775 | 7.4 | 7.5667 | 7.4167 | 7.85 | 7.32 | 6.525 | 6.4333 | 7.4373 | 6 | 8.9 | 51
| Org. Carbon (diss @ 254nm) | Abs 10cm | 0.88635 | 0.89447 | 0.90217 | 0.85924 | 0.72753 | 0.75345 | 0.79552 | 0.83202 | 0.87125 | 0.87442 | 0.7529 | 0.75493 | 0.82489 | 0.6866 | 1.1294 | 48
| UV@254/Raw DOC | ratio | 0.10666 | 0.11045 | 0.11954 | 0.11429 | 0.10747 | 0.10223 | 0.10525 | 0.11331 | 0.11129 | 0.12034 | 0.1155 | 0.11739 | 0.11182 | 0.094707 | 0.16609 | 48
| Phosphate(ortho) | µg/L P | 18 | 23 | 9 | 7.75 | 8.25 | 5.25 | 5.2 | 5.75 | 10.25 | 13 | 13.75 | 13.3333 | 9.7907 | <2 | 23 | 43
| Phosphate(total) | µg/L P | 47.3333 | 46 | 39.6667 | 64.25 | 99.25 | 98.75 | 106.8 | 108 | 110 | 100.8 | 58.5 | 55.3333 | 83.3182 | 39 | 176 | 44
| Silica (SiO3) | mg/L | 7.9425 | 8.665 | 9.3275 | 7.976 | 6.31 | 7.125 | 9.112 | 11.0525 | 11.6175 | 11.488 | 10.165 | 10.86 | 9.3115 | 5.78 | 12.34 | 48
| Sulphide | µg/L | <75 | <75 | <75 | <75 | <75 | <75 | <75 | <75 | <75 | <75 | <75 | <75 | <75 | <75 | <75 | 46
Continued...
2001 - BUFFALO POUND WATER QUALITY DATA
RAW LAKE WATER
page 2
| Parameters | Units | JAN Avg | FEB Avg | MAR Avg | APR Avg | MAY Avg | JUN Avg | JUL Avg | AUG Avg | SEP Avg | OCT Avg | NOV Avg | DEC Avg | YEAR AVG | YEAR MIN | YEAR MAX
TRACE CONSTITUENTS
PreFM
| TTHM's (total) | µg/L(calc) | 23.2 | 21 | 23 | 30.5 | 33.75 | 37.5 | 47.6 | 46.25 | 37.75 | 29.8 | 21.25 | 24 | 31.64 | 18 | 52
| Chloroform | µg/L | 15.4 | 14 | 15.5 | 21.25 | 22.75 | 24.25 | 31.8 | 32.75 | 27.25 | 21.6 | 14.5 | 16.25 | 21.68 | 12 | 37 | 49
| Bromodichloromethane | µg/L | 6.6 | 6 | 6.25 | 7.75 | 9 | 10.75 | 12.6 | 11.5 | 8.75 | 7 | 5.5 | 6 | 8.22 | 5 | 14 | 49
| Chlorodibromomethane | µg/L | 1.2 | 1 | 1.25 | 1.5 | 2 | 2.5 | 3 | 2 | 1.75 | 1.2 | 1.25 | 1.75 | 1.72 | 1 | 4 | 49
| Bromoform | µg/L | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | 1 | 49
BIOLOGICAL
| Blue Green Algae (x10^-3) | per litre | <20 | <20 | <20 | <20 | 50.55 | 2079.8 | 1655 | 2890 | 9092.5 | 9912 | 73.3333 | 26.6667 | 2404.0723 | <20 | 15120 | 47
| Green Algae (x10^-3) | per litre | 680 | 620 | 3622.5 | 10032 | 1385 | 1340 | 1165 | 1310 | 1100 | 680 | 500 | 540 | 2147.8723 | 360 | 16540 | 47
| Diatoms (x10^-3) | per litre | 30 | <20 | 25 | 228 | 240 | 275 | 505 | 565 | 265 | 132 | 80 | 106.6667 | 212.766 | <20 | 1300 | 47
| Flagellates (x10^-3) | per litre | 195 | 120 | 907.5 | 2320 | 1890 | 1675 | 2580 | 3780 | 885 | 112 | 1086.6667 | 2186.6667 | 1489.1489 | 60 | 4420 | 47
| Crustaceans | per litre | 14 | 18 | 33 | 75 | 32.5 | 82.3333 | 58.25 | 113.25 | 232.5 | 104 | 26.3333 | 68 | 75.1136 | <3 | 420 | 44
| Nematodes (x10^-3) | per litre | <20 | <20 | <20 | <20 | <20 | <20 | <20 | <20 | <20 | <20 | <20 | <20 | <20 | <20 | <20 | 47
| Rotifers (x10^-3) | per litre | <20 | <20 | <20 | <20 | <20 | <20 | <20 | <20 | <20 | <20 | <20 | <20 | <20 | <20 | 20 | 47
| Other (x10^-3) | per litre | <20 | <20 | <20 | <20 | <20 | <20 | <20 | <20 | <20 | <20 | <20 | <20 | <20 | <20 | <20 | 47
| Total Green & B-G | per litre | 680 | 626.6667 | 3622.5 | 10040 | 1435.55 | 3419.8 | 2820 | 4200 | 10192.5 | 10592 | 573.3333 | 566.6667 | 10604 | 7660 | 16540
BACTERIOLOGICAL
| Total Coliforms | per 100 ml | 2.4 | 0.83333 | 0.875 | 4.3 | 19.75 | 8.75 | 97.6 | 243.75 | 116.75 | 34.1 | 9.375 | 6.675 | 45.4549 | <1 | 600 | 50
| Faecal Coliforms | per 100 ml | <1 | <1 | <1 | <1 | 1.625 | 1.6375 | 5.08 | 8.375 | 8.375 | 10.94 | <1 | <1 | 3.2186 | <1 | 25.2 | 50
| E. coli | per 100 ml
| Faecal Streptococci | per 100 ml | <1 | <1 | <1 | 96.2 | 6 | 3.5 | 23.6 | 28.75 | 68.25 | 78.8 | 13.75 | 5 | 29.8 | <1 | 472 | 50
| Standard Plate Count | per 1 ml | 37.2 | 25.3667 | 14.875 | 353.44 | 51.3 | 916.5 | 422 | 515.75 | 572 | 285.48 | 305.6667 | 166.5 | 308.628 | 11.6 | 3426 | 49
CHEMICAL DOSES
| Alum | mg/L | 60 | 60 | 65 | 72.1 | 67.5 | 67.5 | 70 | 80 | 85 | 86.8 | 67.5 | 58.75 | 70.3824 | 55 | 100 | 50
| Alum\Raw DOC | ratio | 7.2399 | 7.5031 | 8.4433 | 9.6566 | 9.9632 | 9.1625 | 9.261 | 10.8941 | 10.8906 | 11.8759 | 10.4128 | 8.817 | 9.5639 | 6.7416 | 13.3333
| Chlorine-pre | mg/L | 3.96 | 4.5333 | 4.1575 | 5.28 | 3.75 | 3.15 | 4.52 | 4.675 | 5.025 | 3.3 | 2.525 | 3.3 | 4.0241 | 1.6 | 5.5 | 50
| Chlorine-intermed | mg/L | [15 empty] | 0
| Chlorine-post | mg/L | [5 empty] | 1.225 | 1.46 | 1.175 | 1.15 | 1.2 | 1.4 |  | 1.268 | 1 | 1.6 | 25
| Fluoride (Set Point for MJ) | mg/L | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 50
| Powdered Carbon | mg/L | [15 empty] | 0
| Total Chlorine dose | mg/L (Calc) | 3.96 | 4.5333 | 4.1575 | 5.28 | 3.75 | 4.375 | 5.98 | 5.85 | 6.175 | 4.5 | 3.575 | 3.3 | 4.6457 | 2.8 | 6.7 | 50
| Date GAC`s ON | [5 empty] | 37042 | [7 empty] | 2001-05-31 |  |  | 1
| Date GAC`s OFF | [11 empty] | 37215 |  | 2001-11-20 |  |  | 1
| Date Ice ON Lake | [11 empty] | 37222 |  | 2001-11-27 |  |  | 1
| Date Ice OFF Lake |  |  |  |  | 37008 | [8 empty] | 2001-04-27 |  |  | 1
| Date PAC ON |  |  |  |  | 36984 | [8 empty] | 2001-04-03 |  |  | 1
| Date PAC OFF |  |  |  |  | 37011 | [8 empty] | 2001-04-30 |  |  | 1
0
| Chlorine Residuals Exit Plant (week avg.) | [16 empty] | 0
| Free Chlorine | mg/L | 1.116 | 1.0775 | 1.0362 | 1.0125 | 1.0475 | 0.9625 | 0.994 | 1.0725 | 1.085 | 1.092 | 1.1025 | 1.17 | 1.0642 | 0.93 | 1.19 | 50
| Combined Chlorine | mg/L | 0.424 | 0.435 | 0.44625 | 0.3675 | 0.315 | <0.05 | 0.064 | 0.0975 | 0.125 | 0.128 | 0.2075 | 0.3075 | 0.24088 | <0.05 | 0.58 | 50
2001 - BUFFALO POUND WATER QUALITY DATA
TREATED WATER
page 3
| Parameters | Units | JAN Avg | FEB Avg | MAR Avg | APR Avg | MAY Avg | JUN Avg | JUL Avg | AUG Avg | SEP Avg | OCT Avg | NOV Avg | DEC Avg | YEAR AVG | YEAR MIN | YEAR MAX
PHYSICAL
| Colour (Apparent) | Pt/Co | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5 | 49
| Conductivity | µS/cm | 719.2 | 737 | 754.75 | 699.25 | 601.75 | 613.25 | 581.6 | 546.25 | 548.5 | 560 | 568 | 604.6667 | 625.6327 | 536 | 762 | 49
| Diss. Oxygen | mg/L | 12.62 | 11.9 | 11.675 | 12.02 | 10.225 | 9.325 | 8.56 | 8.65 | 9.675 | 11.16 | 12.95 | 12.875 | 10.9608 | 8.2 | 13.5 | 50
| % Sat. Diss. Oxygen | % | 94.041 | 89.4506 | 88.7587 | 97.6019 | 97.8149 | 97.6401 | 96.303 | 97.8285 | 97.4718 | 93.9369 | 95.1082 | 100.6995 | 95.6677 | 80.7927 | 119.8858 | 50
| Odour (Chlorinated) | T.O.N. | [15 empty] | 0
| Odour(Dechlorinated) | T.O.N. | 4.25 | 5.5 | 8.6667 | 15.6 | 10.75 | <1 | 0.8 | 2.5 | 5.5 | 6.4 | 6 | 14.6667 | 6.617 | <1 | 23 | 47
| PreGAC Odour | T.O.N. | [5 empty] | 70.75 | 97.6 | 69.75 | 65.75 | 26 | 12.3333 |  | 59.2 | 11 | 133 | 25
| Odour Removal by Coagulation and Filtration | % | 68.38% | 58.33% | 57.14% | 84.05% | 87.82% | 63.47% | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | 94% | 47
| Odour Removal Overall | % | 68.38% | 58.33% | 57.14% | 84.05% | 87.82% | 100% | 99.36% | 97.7% | 93.87% | 81.11% | 72.83% | <1 | 80.75% | <1 | 100% | 47
| Particles | per 10 ml | 100.25 | 170 | 227 | 365 | 171.2125 | 403.845 | 333 | 129.25 | 83.5 | 63 | 54 | 117.3333 | 188.7912 | 35 | 689 | 42
| pH | pH units | 7.358 | 7.3 | 7.26 | 7.35 | 7.3025 | 7.445 | 7.444 | 7.215 | 7.2075 | 7.248 | 7.26 | 7.2675 | 7.3084 | 7.08 | 7.64 | 50
| Coagulation pH (Channel 1) | pH units | 7.124 | 7.05 | 7.0725 | 7.04 | 7.0575 | 7.0825 | 7.024 | 6.9425 | 6.88 | 6.948 | 6.99 | 7.1633 | 7.0282 | 6.78 | 7.25 | 49
| SST | mg/L | 0.33333 | 0.45 | 0.5 | 0.3 | 0.225 | 0.275 | 0.22 | 0.35 | 0.3 | 0.3 | 0.325 | 0.53333 | 0.32727 | <0.1 | 0.7 | 44
| SSV | mg/L | 0.16667 | 0.25 | 0.3 | 0.26667 | 0.325 | 0.175 | 0.16 | 0.25 | 0.2 | 0.22 | 0.25 | 0.26667 | 0.23182 | <0.1 | 0.7 | 44
| SSF | mg/L | 0.16667 | 0.2 | 0.2 | <0.1 | 0.125 | 0.1 | 4.24 | 0.1 | 0.1 | 0.08 | 0.075 | 0.26667 | 0.59091 | <0.1 | 20.9 | 44
| Temperature | ° C | 3.08 | 3.4 | 3.825 | 6.36 | 13.3 | 17.5 | 21.1 | 21.375 | 15.675 | 8.08 | 2.55 | 4.9 | 10.1922 | 0.5 | 23.4 | 50
| Turbidity | NTU | 0.094 | 0.073333 | 0.09 | 0.082 | 0.07 | 0.085 | 0.11 | 0.0925 | 0.0925 | 0.088 | 0.0875 | 0.145 | 0.092941 | 0.06 | 0.15 | 50
| Dissolved Solids | mg/L(calc) | 559.01 | #VALUE! | 586.075 | 543.54 | 454.16 | 464.605 | 323.3075 | 401.1425 | 404.3525 | 414.268 | 425.465 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| Particle Log Removal | (calc) | 2.0235 | 1.9119 | 2.1979 | 2.2378 | 2.5359 | 2.1208 | 2.2236 | 2.5158 | 2.6846 | 2.868 | 2.895 | 2.105 | 2.3889 | 1.8705 | 3.128
| Turbidity Log Removal | (calc) | 1.365 | 1.4672 | 1.3575 | 1.7656 | 2.0423 | 2.1631 | 1.9843 | 2.0692 | 1.9379 | 2.0024 | 1.946 | 1.3256 | 1.7913 | 1.0887 | 2.3268
| Langelier Index (RTW) | pH units (calc) | -0.33904 | -0.4582 | -0.39664 | -0.33104 | -0.41557 | -0.20722 | -0.2733 | -0.57647 | -0.67275 | -0.68417 | -0.6762 | -0.53776 | -0.46456 | -0.86579 | -0.056593
MAJOR CONSTITUENTS
| Alkalinity(p) | mg/L CaCO3 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | 50
| Alkalinity(total) | mg/L CaCO3 | 170 | 174 | 180.75 | 162.4 | 132.75 | 132.5 | 114.6 | 99.25 | 100 | 109.2 | 126.25 | 145.6667 | 136.52 | 94 | 182 | 50
| Bicarbonate | mg/L | 207.2 | 212 | 220.25 | 198 | 162 | 161.25 | 139.4 | 120.75 | 121.75 | 133 | 153.75 | 177.6667 | 166.32 | 114 | 222 | 50
| Carbonate | mg/L | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | 50
| Calcium | mg/L | 60.75 | 62.5 | 65.25 | 61.8 | 51.5 | 52.25 | 45 | 43 | 42.25 | 45.4 | 48.25 | 52.3333 | 52 | 42 | 66 | 48
| Magnesium | mg/L | 26.75 | 27 | 27.25 | 25.4 | 20.25 | 20.5 | 20.4 | 19.25 | 20 | 20 | 20 | 21.6667 | 22.1667 | 17 | 28 | 48
| Hardness (total) | mg/L CaCO3 | 261.75 | 268 | 276 | 258.6 | 212 | 213.75 | 197.2 | 186.25 | 187.5 | 195.8 | 202 | 221 | 221.125 | 185 | 279 | 48
| Sodium | mg/L | 53.75 | 54 | 54.75 | 51.4 | 43.75 | 45.5 | 43.75 | 40.75 | 39.75 | 38.6 | 38.5 | 41 | 45.1702 | 38 | 56 | 47
| Potassium | mg/L | 6.35 | 6.95 | 5.525 | 5.26 | 4.775 | 5.075 | 4.925 | 4.6 | 4.4 | 4.18 | 4 | 4.1667 | 4.9404 | 4 | 7.6 | 47
| Sulphate | mg/L | 177.75 | 182.5 | 186.25 | 176 | 151.75 | 157.75 | 152 | 147 | 149 | 147.6 | 137.25 | 141 | 158.3191 | 132 | 188 | 47
| Chloride | mg/L | 17.35 | 17.75 | 17.775 | 18.04 | 14.6 | 15.525 | 16.75 | 15.675 | 15.875 | 14.76 | 13.65 | 14.1 | 15.9702 | 13.4 | 19 | 47
TRACE CONSTITUENTS
CLEAR WELL
| Aluminum (dissolved 0.45µ) | µg/L Chart | 48 | 86.5 | 49.25 | 24.75 | 24 | 27.75 | 31.25 | 11.5 | 6.75 | 6.4 | 18.75 | 57 | 29.617 | <6 | 114 | 47
| Aluminum (total) | µg/L Chart | 97.4 | 100 | 74.5 | 40.25 | 27.75 | 35.25 | 38 | 14 | 11 | 10.2 | 35.75 | 115.5 | 46.9362 | 6 | 167 | 46 | JAN 00 Avg | FEB 00 Avg | MAR 00 Avg | APR 00 Avg | MAY 00 Avg | JUN 00 Avg | JUL 00 Avg | AUG 00 Avg | SEP 00 Avg | OCT 00 Avg | NOV 00 Avg | DEC 00 Avg
| Aluminum (total 12 mo avg) | µg/L | 58.8681 | 54.4097 | 53.0764 | 53.8056 | 53.7847 | 55.4722 | 56.5556 | 56.5556 | 56.5 | 55.7167 | 47.425 | 49.9667 |  |  |  | 0 | 143.8 | 153.5 | 90.5 | 31.5 | 28 | 15 | 25 | 14 | 11.6667 | 19.6 | 135.25 | 85
| Aluminum (particulate) | µg/L (Calc) | 49.4 | 41 | 25.25 | 15.5 | <6 | 7.5 | 6.75 | <6 | <6 | <6 | 17 | 77.6667 | 18.913 | <6 | 106 | 46
| Mixed Media Filter 1 | [16 empty] | 0
| Aluminum (total) | µg/L | 135 | 133 | 98.3333 |  | 43.5 | 42 | 60.5 | 41.6667 | 26 | 61 | 74.25 | 145 | 77.7949 | 26 | 207 | 39
| Mixed Media Filter 12 | [16 empty] | 0
| Aluminum (total) | µg/L | 82.8 | 83.5 | 62 | 24.3333 | 23.5 | 30.3333 | 72 | 31.25 | 24.75 | 36.2 | 51.75 | 66 | 48.5556 | 11 | 143 | 45
| PREGAC | [16 empty] | 0
| Aluminum (dissolved) | µg/L | [5 empty] | 38.5 | 57 | 25.5 | 19.25 | 29.2 | 41 |  | 34.5833 | 18 | 120 | 24
| Aluminum (total) | µg/L Chart | [5 empty] | 41.75 | 64 | 31.25 | 26.5 | 54 | 58.6667 |  | 45.8333 | 22 | 131 | 24
46
| Ammonia N | mg/L N | <0.04 | <0.04 | <0.04 | <0.04 | 0.04 | <0.04 | 0.058 | 0.0375 | 0.0575 | 0.082 | 0.0675 | 0.053333 | 0.043953 | <0.04 | 0.13 | 43
| Bromide | mg/L | <0.06 | <0.06 | <0.06 | <0.06 | <0.06 | <0.06 | <0.06 | <0.06 | <0.06 | <0.06 | <0.06 | <0.06 | <0.06 | <0.06 | <0.06 | 47
| Fluoride | mg/L | 0.134 | 0.13667 | 0.14 | 0.12 | 0.115 | 0.1275 | 0.134 | 0.1225 | 0.125 | 0.13 | 0.125 | 0.14333 | 0.129 | 0.1 | 0.15 | 50
| Fluoride (actual MJ dose) | mg/L (wk avg) | 0.97 | 0.96667 | 0.98 | 0.972 | 1.0675 | 1.1225 | 0.984 | 1.0425 | 1.0075 | 1.012 | 1.0475 | 1.065 | 1.018 | 0.78 | 1.2 | 50
| Iron (dissolved) | mg/L | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | 0.02 | 42
| Iron (total) | mg/L | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | 0.03 | 42
| Manganese (dissolved) | mg/L | <0.01 | <0.01 | <0.01 | <0.01 | <0.01 | <0.01 | <0.01 | <0.01 | <0.01 | <0.01 | <0.01 | <0.01 | <0.01 | <0.01 | 0.01 | 42
| Manganese (total) | mg/L | <0.01 | <0.01 | <0.01 | <0.01 | <0.01 | <0.01 | <0.01 | <0.01 | <0.01 | <0.01 | <0.01 | <0.01 | <0.01 | <0.01 | 0.01 | 42
| Nitrate | mg/L N | 0.0675 | 0.135 | 0.2 | <0.06 | <0.06 | <0.06 | <0.06 | <0.06 | <0.06 | <0.06 | <0.06 | <0.06 | <0.06 | <0.06 | 0.23 | 47
| Organic N | mg/L N | 0.275 | 0.24 | 0.20333 | 0.2425 | 0.2525 | 0.0625 | 0.074 | 0.0975 | 0.2 | 0.198 | 0.22 | 0.26 | 0.18233 | 0.05 | 0.36 | 43
| CW TOC | mg/L C(UV) | 5.42 | 5.5 | 5.45 | 4.66 | 4.175 | 1.1 | 1.5667 | 2.25 | 2.775 | 2.98 | 3.55 | 4.3333 | 3.624 | 1 | 5.6 | 50
| CW DOC (GF diss) | mg/L C(UV) | 5.38 | 5.5 | 5.4 | 4.58 | 4.25 | 1.075 | 1.5333 | 2.2167 | 2.85 | 2.96 | 3.6 | 4.2667 | 3.6471 | 1 | 5.6 | 51
| PreGAC DOC (GF diss) | mg/L C(UV) | [5 empty] | 4.525 | 4.6 | 4.4 | 4.525 | 4.4 | 4.1 |  | 4.428 | 3.9 | 4.9 | 25
| DOC Removal by Coagulation & Filtration | % Removal | 35.11% | 31.43% | 29.94% | 39.26% | 37.23% | 38.65% | 39.23% | 40.69% | 42.43% | 39.9% | 35.97% | 33.67% | 37.19% | 26.76% | 50% | 51
| DOC Removal by GAC Filtration | % Removal | [5 empty] | 76.23% | 66.56% | 49.43% | 37.12% | 32.62% | 18.68% |  | 46.75% | 14.29% | 78.26% | 25
| Total DOC (% Removal) | % Removal | 35.11% | 31.43% | 29.94% | 39.26% | 37.23% | 85.43% | 79.71% | 70.09% | 63.76% | 59.55% | 44.8% | 33.67% | 50.99% | 26.76% | 86.84% | 51
| CW Organic Carbon (diss @ 254nm) | Abs 10cm | 0.54565 | 0.5522 | 0.55458 | 0.44236 | 0.39313 | 0.018325 | 0.06228 | 0.12752 | 0.17205 | 0.1823 | 0.28282 | 0.43303 | 0.30136 | 0.0019 | 0.5737 | 49
| UV@254/CW DOC | ratio | 0.10108 | 0.10101 | 0.10274 | 0.095674 | 0.092593 | 0.017034 | 0.035443 | 0.055434 | 0.060412 | 0.061662 | 0.077243 | 0.10149 | 0.073419 | 0.0019 | 0.10825 | 49
| PreGAC Organic Carbon (diss @ 254nm) | Abs 10cm | [5 empty] | 0.41337 | 0.42786 | 0.4319 | 0.42247 | 0.39748 | 0.4025 |  | 0.41621 | 0.385 | 0.4636 | 25
| Phosphate(ortho) | µg/L P | 5 | 5 | 4 | 2.5 | 2 | 21 | 7 | 3.75 | 5.25 | 4 | 4 | 2.3333 | 5.6512 | <2 | 44 | 43
| Phosphate(total) | µg/L P | 12.3333 | 9 | 9.3333 | 7.5 | 5.75 | 24.5 | 12 | 8 | 5.25 | 4.8 | 4.5 | 6.6667 | 9.0909 | 3 | 50 | 44
| Silica (SiO3) | mg/L | 7.81 | 8.195 | 9.025 | 7.64 | 5.535 | 6.755 | 8.26 | 10.1175 | 11.3275 | 10.728 | 10.065 | 9.97 | 8.7912 | 5.33 | 12.09 | 48
| Sulphide | µg/L | <75 | <75 | <75 | <75 | <75 | <75 | <75 | <75 | <75 | <75 | <75 | <75 | <75 | <75 | <75 | 46
Continued...
2001 - BUFFALO POUND WATER QUALITY DATA
TREATED WATER
page 4
| Parameters | Units | JAN Avg | FEB Avg | MAR Avg | APR Avg | MAY Avg | JUN Avg | JUL Avg | AUG Avg | SEP Avg | OCT Avg | NOV Avg | DEC Avg | YEAR AVG | YEAR MIN | YEAR MAX
TRACE CONSTITUENTS
CLEARWELL
| TTHM's (total) | µg/L(calc) | 33.4 | 31 | 30 | 30.75 | 41.25 | 1 | 9.8 | 45.75 | 46.75 | 40 | 30.25 | 28.25 | 31.7292 | 1 | 52
| Chloroform | µg/L | 20.8 | 18.6667 | 19 | 20 | 26.75 | <1 | 9.2 | 39.75 | 36 | 29 | 21.75 | 19.25 | 21.66 | <1 | 43 | 49
| Bromodichloromethane | µg/L | 10.6 | 10.3333 | 9 | 9 | 12.25 | <1 | <1 | 5.5 | 9.5 | 9.6 | 7.5 | 7 | 7.46 | <1 | 13 | 49
| Chlorodibromomethane | µg/L | 2 | 2 | 2 | 1.75 | 2.25 | <1 | <1 | <1 | 1 | 1.2 | 1 | 2 | 1.3 | <1 | 3 | 49
| Bromoform | µg/L | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | 1 | 49
CHANNEL
| TTHM's (total) | µg/L(calc) | 30.6 | 30.6667 | 30.25 | 29.25 | 37.5 | 41.5 | 53 | 51.5 | 42.75 | 33.4 | 24 | 25.5 | 36.12 | 20 | 58
| Chloroform | µg/L | 18.8 | 18 | 18.75 | 18.75 | 24.25 | 26.25 | 35.4 | 36.5 | 31 | 23.6 | 16.5 | 17 | 23.98 | 14 | 40 | 49
| Bromodichloromethane | µg/L | 9.8 | 10.6667 | 9.5 | 8.75 | 11 | 12.5 | 14.4 | 13 | 10 | 8.2 | 6 | 6.5 | 10.06 | 5 | 16 | 49
| Chlorodibromomethane | µg/L | 2 | 2 | 2 | 1.75 | 2.25 | 2.75 | 3.2 | 2 | 1.75 | 1.6 | 1.5 | 2 | 2.08 | 1 | 4 | 49
| Bromoform | µg/L | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | 49
PreGAC
| TTHM's (total) | µg/L(calc) | [5 empty] | 40.25 | 53.8 | 54.25 | 43.25 | 35.2 | 24.3333 |  | 42.76 | 20 | 59
| Chloroform | µg/L | [5 empty] | 25.25 | 36 | 39.25 | 31.25 | 25 | 16.6667 |  | 29.52 | 14 | 40
| Bromodichloromethane | µg/L | [5 empty] | 12 | 14.6 | 13.5 | 10 | 8.6 | 6.3333 |  | 11.08 | 5 | 17
| Chlorodibromomethane | µg/L | [5 empty] | 2.75 | 3.2 | 1.5 | 2 | 1.6 | 1.3333 |  | 2.12 | <1 | 4
| Bromoform | µg/L | [5 empty] | <1 | <1 | <1 | <1 | <1 | <1 |  | <1 | <1 | 1
BIOLOGICAL
| Blue Green Algae | per litre | <200 | <200 | 300 | 160 | 400 | 6250 | 8350 | 14650 | 13200 | 4240 | 955 | 666.6667 | 4179.5833 | <200 | 41800 | 48
| Green Algae | per litre | 12250 | 23066.6667 | 37650 | 39600 | 150 | 1450 | 7600 | 9450 | 450 | 320 | 550 | 1533.3333 | 11491.6667 | <200 | 112800 | 48
| Diatoms | per litre | <200 | <200 | <200 | <200 | <200 | 300 | 800 | 300 | 400 | 360 | <200 | 266.6667 | 220.8333 | <200 | 1400 | 48
| Flagellates | per litre | <200 | <200 | <200 | <200 | <200 | <200 | <200 | <200 | <200 | <200 | <200 | 200 | <200 | <200 | 400 | 48
| Crustaceans | per litre | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | <2 | 48
| Nematodes | per litre | <200 | <200 | <200 | <200 | <200 | <200 | <200 | <200 | <200 | <200 | <200 | <200 | <200 | <200 | <200 | 48
| Rotifers | per litre | <200 | <200 | <200 | <200 | <200 | <200 | <200 | 150 | 250 | <200 | <200 | <200 | <200 | <200 | 400 | 48
| Other | per litre | <200 | <200 | <200 | <200 | <200 | <200 | <200 | <200 | <200 | <200 | <200 | <200 | <200 | <200 | <200 | 48
BACTERIOLOGICAL
| Total Coliforms | per 100 ml | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | 50 | 200
* | Faecal Coliforms | per 100 ml | [15 empty] | 0
| Faecal Streptococci | per 100 ml | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | 50 | 200
| Standard Plate Count | per 1 mL | <0.1 | <0.1 | <0.1 | <0.1 | <0.1 | 0.115 | 8.96 | 10.1 | 3.625 | 1.24 | 0.255 | <0.1 | 2.1139 | <0.1 | 35 | 50 | 250
*Note: Faecal Coliforms analyzed ONLY if Total Coliforms Detected.
Total Tests Done
6672
Note on B184: These values are averaged with results from the previous year which are located in the range CW AL PREYEAR. Example: Total Aluminum average for June is calculated by averaging Jan to June of this year and July to Dec of the previous year.

## DOC % Removal
35796

## RTW
| The RTW Model Ver. 2.0 |  | ID: | XYZ Water Co., Sample Point 3b, 8/12/93 | [17 empty] | PRINT | CHEMLIST |  |  |  |  | Chemicals Available for Use in RTW Model
[9 empty] | Interim | Interim | Final | Final | Final | Final | Tk | 275.3 | [5 empty] | /AIWYSIWYG~P{EDIT}RSA1..J41~G | {GOTO}BA1~
| STEP 1: Enter initial water characteristics. |  |  |  | STEP 2: Enter amount of each chemical |  |  |  | Acd, mg/l | pH | Acd, mg/l | pHs | Ca, mg/l | Alk, mg/l | I | 0.011843 | [8 empty] | Indicate with a Y those chemicals which you want to include in the input area.
| Measured TDS | 473.73 | mg/L |  | to be added (expressed as 100% chemical). | [9 empty] | E | 86.8361 | [8 empty] | Up to 10 may be used at one time. Press HOME to return to the main screen.
| Measured temperature | 2.3 | deg C |  | Press Alt+C to select chemicals for this list. |  |  |  | #N/A | 14 | #N/A | #N/A | #N/A | #N/A | A | 0.49239
| Measured pH | 7.3 |  |  | Calcium hypochlorite | 0 | mg/L |  | #N/A | 13 | #N/A | #N/A | #N/A | #N/A | f(I) | 0.098146 | [7 empty] | Y or N? |  |  |  | Chemical Name | Alk | Acd | Ca | Cl | SO4 | dose | Alk | Acd | Ca | Cl | SO4
| Measured alk, as CaCO3 | 151 | mg/L |  | Carbon dioxide | 0 | mg/L |  | #N/A | 12 | #N/A | #N/A | #N/A | #N/A | K1 | 2.8146e-07 |  | Forms of CaCO3 and their solubility product constants | [6 empty] | y | 1 | 1 | Alum *18H2O | -0.45 | 0.45 | 0 | 0 | 0.43 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
54 | Measured Ca, as CaCO3 | 135 | mg/L |  | Caustic soda | 0 | mg/L |  | #N/A | 11 | #N/A | #N/A | #N/A | #N/A | K2 | 2.5368e-11 | Form # | 1 | 2 | 3 | 4 |  |  |  | n | 0 | 1 | Alum 50% solution | -0.24 | 0.24 | 0 | 0 | 0.23 | 0 | 0 | 0 | 0 | 0 | 0
| Measured Cl | 14.4 | mg/L |  | Ferrous sulfate *7H2O | 0 | mg/L |  | #N/A | 10 | #N/A | #N/A | #N/A | #N/A | Kw | 1.4139e-15 | Preferred | Calcite | Aragonite | Vaterite | General |  |  |  | n | 0 | 1 | Aluminum Chloride | -1.12 | 1.12 | 0 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Measured SO4 | 142 | mg/L |  | Hydrochloric acid | 0 | mg/L |  | #N/A | 9 | #N/A | #N/A | #N/A | #N/A | Ks | 4.1067e-09 | 1 | 4.1067e-09 | 5.9577e-09 | 1.7598e-08 | 8.7658e-09 |  |  |  | n | 0 | 1 | Calcium carbonate | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| For CT and TTHM functions enter current: |  |  |  | Hydrofluosilicic acid | 0 | mg/L |  | #N/A | 8 | #N/A | #N/A | #N/A | #N/A | fm | 0.90204 | [8 empty] | n | 0 | 1 | Calcium chloride | 0 | 0 | 0.9 | 0.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Treated water pH |  |  | ???? | Quicklime | 0 | mg/L |  | #N/A | 7 | #N/A | #N/A | #N/A | #N/A | fd | 0.66207 | [8 empty] | n | 0 | 1 | Calcium hypochlorite | 0.7 | -0.7 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Chlorine residual |  | mg/L |  | Soda ash | 0 | mg/L |  | #N/A | 6 | #N/A | #N/A | #N/A | #N/A | K1p | 3.4591e-07 | [8 empty] | y | 1 | 2 | Carbon dioxide | 0 | 2.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Chlorine or hypochlorite dose |  |  |  | Sodium hypochlorite | 0 | mg/L |  | #N/A | 5 | #N/A | #N/A | #N/A | #N/A | K2p | 3.8316e-11 | [8 empty] | y | 1 | 3 | Caustic soda | 1.25 | -1.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| as chlorine equivalent |  | mg/L |  | User specified* | 0 | mg/L |  | #N/A | 4 | #N/A | #N/A | #N/A | #N/A | Kwp | 1.7377e-15 | [8 empty] | y | 1 | 4 | Chlorine gas | -1.41 | 1.41 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | #N/A | 3 | #N/A | #N/A | #N/A | #N/A | Ksp | 9.3688e-09 | [8 empty] | n | 0 | 4 | Ferric chloride | -0.93 | 0.93 | 0 | 0.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STEP 3: Adjust at Step 2 until interim water characteristics meet your criteria. | [7 empty] | #N/A | 2 | [14 empty] | n | 0 | 4 | Ferric sulfate *9H2O | -0.53 | 0.53 | 0 | 0 | 0.51 | 0 | 0 | 0 | 0 | 0 | 0
| Theoretical interim water characteristics |  |  | Desired | Theoretical interim water characteristics |  |  | Desired | #N/A | 1 | #N/A | #N/A | #N/A | #N/A | [10 empty] | n | 0 | 4 | Ferrous sulfate *7H2O | -0.36 | 0.36 | 0 | 0 | 0.36 | 0 | 0 | 0 | 0 | 0 | 0
| Interim alkalinity | #N/A | mg/L | > 40 mg/L | Interim pH | #N/A |  | 6.8-9.3 |  |  | #N/A | #N/A | #N/A | #N/A | [10 empty] | y | 1 | 5 | Hydrochloric acid | -1.37 | 1.37 | 0 | 0.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interim Ca, as CaCO3 | #N/A | mg/L | > 40 mg/L | Precipitation potential | #N/A | mg/L | 4-10 mg/L | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [10 empty] | y | 1 | 6 | Hydrofluosilicic acid | -2.08 | 2.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Alk/(Cl+SO4) | #N/A |  | > 5.0 | Langelier index | #N/A |  | >0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [10 empty] | y | 1 | 7 | Lime (slaked) | 1.35 | -1.35 | 1.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Press PAGE DOWN for additional initial, interim and final water characteristics if desired. | [7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [10 empty] | n | 0 | 7 | Phosphoric acid | -1.53 | 1.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [10 empty] | n | 0 | 7 | Potassium Hydroxide | 0.89 | -0.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [10 empty] | n | 0 | 7 | Quicklime | 1.79 | -1.79 | 1.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Calculated initial water characteristics |  |  |  | Theoretical final water characteristics |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [10 empty] | y | 1 | 8 | Soda ash | 0.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Initial acidity | 199.237 | mg/L |  | after CaCO3 precipitation |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [10 empty] | y | 1 | 9 | Sodium bicarbonate | 0.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Initial Ca sat, as CaCO3 | 449.8524 | mg/L |  | Final alkalinity | #N/A | mg/L |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [10 empty] | n | 0 | 9 | Sodium hypochlorite | 0.67 | -0.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Initial DIC, as CaCO3 | 350.237 | mg/L |  | Final Ca | #N/A | mg/L |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [10 empty] | Y | 1 | 10 | Sulfuric Acid | -1.02 | 1.02 | 0 | 0 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Final acidity | #N/A | mg/L |  | #N/A | #N/A | [14 empty] | n | 0 | 10 | Zinc Sulfate | -0.35 | 0.35 | 0 | 0 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0
| Theoretical interim water characteristics |  |  |  | Final pH | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [10 empty] | n | 0 | 10 | User specified* | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Interim acidity | #N/A | mg/L |  | Final DIC, as CaCO3 | #N/A | mg/L |  |  |  | #N/A | #N/A | #N/A | #N/A | [10 empty] | n | 0 | 10 | User specified* | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Interim Ca sat, as CaCO3 | #N/A | mg/L | [5 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [11 empty] | 10 |  | * See User's Manual for information on user specified chemicals
| Ryznar index | #N/A | [6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
| Interim DIC, as CaCO3 | #N/A | mg/L |  | Press PAGE UP to review measured |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [13 empty] | Alt+C to add to list
| Aggressiveness Index | #N/A |  |  | initial water characteristics, chemical |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[5 empty] | addition quantities and additional |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| CT and TTHM Results |  |  |  | interim water characteristics. |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Required chlorine residual to maintain current | [7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| level of giardia inactivation |  | N/A | mg/L |  |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Estimated maximum total trihalomethane concentration change from current level |  |  |  |  | N/A | % |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[9 empty] | #N/A | #N/A
| Macro Menu: Press ALT+P to print spreadsheet to a graphics printer. | [7 empty] | #N/A | #N/A |  | #N/A | #N/A | #N/A

## MACRO
CHOICEPICK | 0
# of weeks in choice | 52
CHOICE | EXIT
2001-01-01
2001-01-08
2001-01-15
2001-01-22
2001-01-29
2001-02-05
2001-02-12
2001-02-19
2001-02-26
2001-03-05
2001-03-12
2001-03-19
2001-03-26
2001-04-02
2001-04-09
2001-04-16
2001-04-23
2001-04-30
2001-05-07
2001-05-14
2001-05-21
2001-05-28
2001-06-04
2001-06-11
2001-06-18
2001-06-25
2001-07-02
2001-07-09
2001-07-16
2001-07-23
2001-07-30
2001-08-06
2001-08-13
| 2001-08-20 |  | {GOTO}CHEMLIST~
2001-08-27
2001-09-03
2001-09-10
2001-09-17
2001-09-24
2001-10-01
2001-10-08
2001-10-15
2001-10-22
2001-10-29
2001-11-05
2001-11-12
2001-11-19
2001-11-26
2001-12-03
2001-12-10
2001-12-17
| 2001-12-24 | {IF @sum(chemlist)>0}{EDIT-CLEAR chemlist;"contents"}
\C | {IF @sum(chemlist)>0}{EDIT-CLEAR chemlist;"contents"}
{CHOOSE-ITEM choice;choicepick;"Which week would you like the Langelier Index determined?";"CHOOSE-WEEK"}
{IF @CELL("TYPE";choicepick)="B"}{QUIT}
{IF choicepick=0}{QUIT}
{GOTO}janwk1~{R +choicepick-1}{D +@ROWS(RN RAWTDS)-1}
{RANGE-NAME-CREATE "checktds"}
{IF checktds=0}{BRANCH alrt1}
{RANGE-NAME-DELETE "checktds"}
RAW DATA | {EDIT-COPY}{EDIT-PASTE-SPECIAL tds;"VALUES"} | COPY TDS
| {U +@ROWS(RN RAWTEMP)-1}{EDIT-COPY}{EDIT-PASTE-SPECIAL temp;"VALUES"} | COPY TEMP
| {U +@ROWS(RN RAWPH)-1}{EDIT-COPY}{EDIT-PASTE-SPECIAL ph;"VALUES"} | COPY pH
| {D +@ROWS(RN RAWALK)-1}{EDIT-COPY}{EDIT-PASTE-SPECIAL alk;"VALUES"} | COPY ALK
| {D +@ROWS(RN RAWCA)-1}{EDIT-COPY}{EDIT-PASTE-SPECIAL ca temp;"VALUES"} | COPY CA
| {D +@ROWS(RN RAWCL)-1}{EDIT-COPY}{EDIT-PASTE-SPECIAL cl;"VALUES"} | COPY CL
| {U +@ROWS(RN RAWSO4)-1}{EDIT-COPY}{EDIT-PASTE-SPECIAL so4;"VALUES"} | COPY SO4
{U +@ROWS(RN RAWLI)-1}{RANGE-NAME-CREATE "li"}
| {EDIT-COPY langindex}{EDIT-PASTE-SPECIAL li;"VALUES"} | COPY LANGIN RTW
{RANGE-NAME-DELETE "li"}
CW DATA | {D +@ROWS(RN CWTDS)-1}
| {EDIT-COPY}{EDIT-PASTE-SPECIAL tds;"VALUES"} | COPY TDS
| {U +@ROWS(RN CWTEMP)-1}{EDIT-COPY}{EDIT-PASTE-SPECIAL temp;"VALUES"} | COPY TEMP
| {U +@ROWS(RN CWPH)-1}{EDIT-COPY}{EDIT-PASTE-SPECIAL ph;"VALUES"} | COPY pH
| {D +@ROWS(RN CWALK)-1}{EDIT-COPY}{EDIT-PASTE-SPECIAL alk;"VALUES"} | COPY ALK
| {D +@ROWS(RN CWCA)-1}{EDIT-COPY}{EDIT-PASTE-SPECIAL ca temp;"VALUES"} | COPY CA
| {D +@ROWS(RN CWCL)-1}{EDIT-COPY}{EDIT-PASTE-SPECIAL cl;"VALUES"} | COPY CL
| {U +@ROWS(RN CWSO4)-1}{EDIT-COPY}{EDIT-PASTE-SPECIAL so4;"VALUES"} | COPY SO4
{U +@ROWS(RN CWLI)-1}{RANGE-NAME-CREATE "li"}
| {EDIT-COPY langindex}{EDIT-PASTE-SPECIAL li;"VALUES"} | COPY LANGIN RTW
{RANGE-NAME-DELETE "li"}{U 152}
{BRANCH \c}
ALRT1 | {ALERT "This week does not have all the information necessary for the calculation of the Langelier Index.";1;NOTE;;}
{RANGE-NAME-DELETE "checktds"}{BRANCH \c}
\0 | {ALERT "Press CNTR C to activate the Langelier Index macro.";1;NOTE;;}
\H | {goto}return home~

## O2 Table
Temperature (°C) | Oxygen Solubility (mg/L)
0 mg/L Chlorinity
0 | 14.64
0.1 | 14.6
0.2 | 14.55
0.3 | 14.51
0.4 | 14.47
0.5 | 14.43
0.6 | 14.39
0.7 | 14.35
0.8 | 14.31
0.9 | 14.27
1 | 14.23
1.1 | 14.19
1.2 | 14.15
1.3 | 14.1
1.4 | 14.06
1.5 | 14.03
1.6 | 13.99
1.7 | 13.95
1.8 | 19.91
1.9 | 13.87
2 | 13.83
2.1 | 13.79
2.2 | 13.75
2.3 | 13.71
2.4 | 13.68
2.5 | 13.64
2.6 | 13.6
2.7 | 13.56
2.8 | 13.52
2.9 | 13.49
3 | 13.45
3.1 | 13.41
3.2 | 13.38
3.3 | 13.34
3.4 | 13.3
3.5 | 13.27
3.6 | 13.23
3.7 | 13.2
3.8 | 13.16
3.9 | 13.12
4 | 13.09
4.1 | 13.05
4.2 | 13..02
4.3 | 12.98
4.4 | 12.95
4.5 | 12.92
4.6 | 12.88
4.7 | 12.85
4.8 | 12.81
4.9 | 12.78
5 | 12.75
5.1 | 12.71
5.2 | 12.68
5.3 | 12.65
5.4 | 12.61
5.5 | 12.58
5.6 | 12.55
5.7 | 12.52
5.8 | 12.48
5.9 | 12.45
6 | 12.42
6.1 | 12.39
6.2 | 12.36
6.3 | 12.32
6.4 | 12.29
6.5 | 12.26
6.6 | 12.23
6.7 | 12.2
6.8 | 12.17
6.9 | 12.14
7 | 12.11
7.1 | 12.08
7.2 | 12.05
7.3 | 12.02
7.4 | 11.99
7.5 | 11.96
7.6 | 11.93
7.7 | 11.9
7.8 | 11.87
7.9 | 11.84
8 | 11.81
8.1 | 11.78
8.2 | 11.75
8.3 | 11.72
8.4 | 11.69
8.5 | 11.67
8.6 | 11.64
8.7 | 11.61
8.8 | 11.58
8.9 | 11.55
9 | 11.53
9.1 | 11.5
9.2 | 11.47
9.3 | 11.44
9.4 | 11.42
9.5 | 11.39
9.6 | 11.36
9.7 | 11.33
9.8 | 11.31
9.9 | 11.28
10 | 11.25
10.1 | 11.23
10.2 | 11.2
10.3 | 11.18
10.4 | 11.15
10.5 | 11.12
10.6 | 11.1
10.7 | 11.07
10.8 | 11.05
10.9 | 11.02
11 | 10.99
12 | 10.777
12.1 | 10.72
12.2 | 10.7
12.3 | 10.67
12.4 | 10.65
12.5 | 10.63
12.6 | 10.6
12.7 | 10.58
12.8 | 10.55
12.9 | 10.53
13 | 10.51
13.1 | 10.48
13.2 | 10.46
13.3 | 10.44
13.4 | 10.41
13.5 | 10.39
13.6 | 10.37
13.7 | 10.35
13.8 | 10.32
13.9 | 10.3
14 | 10.28
14.1 | 10.26
14.2 | 10.23
14.3 | 10.21
14.4 | 10.19
14.5 | 10.17
14.6 | 10.15
14.7 | 10.12
14.8 | 10.1
14.9 | 10.08
15 | 10.06
15.1 | 10.04
15.2 | 10.02
15.3 | 9.99
15.4 | 9.97
15.5 | 9.95
15.6 | 9.93
15.7 | 9.91
15.8 | 9.89
15.9 | 9.87
16 | 9.85
16.1 | 9.83
16.2 | 9.81
16.3 | 9.8
16.4 | 9.76
16.5 | 9.74
16.6 | 9.72
16.7 | 9.7
16.8 | 9.68
16.9 | 9.66
17 | 9.64
17.1 | 9.62
17.2 | 9.6
17.3 | 9.58
17.4 | 9.56
17.5 | 9.54
17.6 | 9.53
17.7 | 9.51
17.8 | 9.49
17.9 | 9.47
18 | 9.45
18.1 | 9.43
18.2 | 9.41
18.3 | 9.39
18.4 | 9.37
18.5 | 9.35
18.6 | 9.33
18.7 | 9.31
18.8 | 9.3
18.9 | 9.28
19 | 9.26
19.1 | 9.24
19.2 | 9.22
19.3 | 9.2
19.4 | 9.19
19.5 | 9.17
19.6 | 9.15
19.7 | 9.13
19.8 | 9.11
19.9 | 9.09
20 | 9.08
20.1 | 9.06
20.2 | 9.04
20.3 | 9.02
20.4 | 9.01
20.5 | 8.99
20.6 | 8.97
20.7 | 8.95
20.8 | 8.94
20.9 | 8.92
21 | 8.9
21.1 | 8.88
21.2 | 8.87
21.3 | 8.85
21.4 | 8.83
21.5 | 8.82
21.6 | 8.8
21.7 | 8.78
21.8 | 8.76
21.9 | 8.75
22 | 8.73
22.1 | 8.71
22.2 | 8.7
22.3 | 8.68
22.4 | 8.66
22.5 | 8.65
22.6 | 8.63
22.7 | 8.62
22.8 | 8.6
22.9 | 8.58
23 | 8.57
23.1 | 8.55
23.2 | 8.53
23.3 | 8.52
23.4 | 8.5
23.5 | 8.49
23.6 | 8.47
23.7 | 8.46
23.8 | 8.44
23.9 | 8.42
24 | 8.41
24.1 | 8.39
24.2 | 8.38
24.3 | 8.36
24.4 | 8.35
24.5 | 8.33
24.6 | 8.32
24.7 | 8.3
24.8 | 8.28
24.9 | 8.27
25 | 8.25
25.1 | 8.24
25.2 | 8.22
25.3 | 8.21
25.4 | 8.19
25.5 | 8.18
25.6 | 8.16
25.7 | 8.15
25.8 | 8.14
25.9 | 8.12
26 | 8.11
26.1 | 8.09
26.2 | 8.08
26.3 | 8.06
26.4 | 8.05
26.5 | 8.03
26.6 | 8.02
26.7 | 8
26.8 | 7.99
26.9 | 7.98
27 | 7.96
27.1 | 7.95
27.2 | 7.93
27.3 | 7.92
27.4 | 7.9
27.5 | 7.89
27.6 | 7.88
27.7 | 7.86
27.8 | 7.85
27.9 | 7.83
28 | 7.82
28.1 | 7.81
28.2 | 7.79
28.3 | 7.78
28.4 | 7.77
28.5 | 7.75
28.6 | 7.74
28.7 | 7.73
28.8 | 7.71
28.9 | 7.7
29 | 7.69
29.1 | 7.67
29.2 | 7.66
29.3 | 7.65
29.4 | 7.63
29.5 | 7.62
29.6 | 7.61
29.7 | 7.59
29.8 | 7.58
29.9 | 7.57
30 | 7.55
Note on A1: blair kardash 01/13/00 02:05:42 PM reference for table: Standard Methods 18th Edition p. 4-101